## RULES FOR FIRE ALARM SYSTEM

- SCOPE:

  - These rules cover the planning, design, selection and installation of fire detection and alarm systems. They are applicable to simple systems with a few manual call points as well as to complex installations comprising detectors; manual call points; control and indicating equipment etc. They covers systems capable of providing signals to initiate, in the event of fire, the operation of ancillary services such as fire extinguishing systems and other necessary precautions, but it does not cover the ancillary services. It covers the fire detection and alarm systems installed in buildings of different types including those installed in industries.

  - Where the use of new materials or inventions lead to departure from these Regulations, the resulting degree of safety provided by such installation has to be not less than that obtained by compliance with these regulations. However, such cases will be considered on their own merits.

+ + + + + + + +

RULES FOR FIRE ALARM SYSTEM

- TERMINOLOGY AND GLOSSARY OF TERMS:

For the regulations on the Fire alarm systems, the following definitions shall apply:

  - ACTIVATION DEVICE:

Device capable of being operated automatically or manually to initiate an alarm of fire, that is, detector, a manual call point or a  pressure switch.

- ADDRESSABLE SYSTEM:

A system in which signals from each detectors and/or call point are individually identified at the control panel.

- AUTOMATIC FIRE ALARM SYSTEM:

Fire alarm system comprising components and sub-systems required for detecting a fire, initiating an automatic alarm for fire and initiating other action as required.

- AUTOMATIC FIRE SIGNAL:

An alarm of fire originated from an automatic device given audibly or visibly or both.

- CONTROL CENTER:

Permanently manned room with qualified staff preferably on ground floor within the premises at risk for the receipt of emergency calls and equipped with communications needed for the transmission of calls for assistance to services such as fire brigade and police.

- CONTROL AND INDICATING EQUIPMENT:

Unit(s) containing the controls, relays, switches, and associated circuits that are necessary to -

- provide power,

- receive signals from alarm initiating devices and                                transmit  them to  the fire alarm services and control for fire protection equipment and

- electrically supervise the system circuitry.

- DETECTOR:

A part of an automatic detection system that contains at least one sensor which constantly or at frequent intervals monitors at least one suitable physical and/or chemical phenomenon associated with fire, and that provides at least one corresponding signal to the control and indicating equipment. Detectors can initiate alarm through anyone of the outputs of combustion i.e. conductive or convective or radiant.

- FAULT SIGNAL:

A distinctive audible and visible signal indicating the occurrence of a fault within the system. (for example break in circuit, short circuit, fault in power supply etc.)

- LINE TYPE DETECTOR:

- Spot Type Detector:

- Air Sampling Type Detector:

- FLOOR:

Area contained on each storey of the building.

- MANUAL CALL POINT:

Manually operated device used to initiate an alarm signal.

- MANUAL SYSTEM:

A system containing no automatic detectors and in which an alarm of fire can only be initiated manually.

- MIMIC PANEL

A panel in which the floor/area plans of the premises are projected to reduced scale to enable easy identification of the sector/zone within the system.

- SEARCH DISTANCE:

The distance, which has to be traveled by searcher within a zone in order to determine visually the position of fire.

- SECTOR:

A Sub-division of the protected premises larger than zone. A larger floor may be demarcated into sectors (i.e. addressed part of the floor). A sector will normally contain many zones.

- SMOKE:

Particulate and aerosol products of combustion generated by a fire, whether this be of the smoldering or open flame type.

- SOUNDER:

An electronic hooter or horn or electric bell associated with the fire alarm system.

- HOOTER OR HORN OR SIREN:

An electronic hooter or horn or electric bell associated with fire alarm system.

- ZONE:

A Sub-division of a sector of protected premises such that the occurrence of a fire within it will be indicated on control and indicating equipment separately and independently and indication of fire in another sub-division (zone).

+ + + +

RULES FOR FIRE ALARM SYSTEM

- GENERAL REQUIREMENTS:

- Plans for submission to the Committee shall be drawn up in    accordance with the following requirements:

- Plans shall be clear, contain all requirement details including scale and point of Compass and shall be dated.

- Plans of new installation shall show the entire compound; all buildings therein, their door and window openings, and the boundary walls. Buildings under construction and future extension envisaged, shall be indicated by the dotted lines. Plans of extensions to approved existing installations need not show the rest of the compound but sufficient details shall be given of the existing installations in correlation to the extension, to enable the Committee’s Inspection staff to check the plans and offer comments. In case of storeyed buildings, drawings submitted shall include plans of each storey together with sectional elevations.

- MATERIAL

Plans shall be on White paper or ammonia paper or Ferro Prussiate paper.

- Plans shall generally be prepared in accordance with IS: 696, shall not exceed 850x1200mm in size and shall be drawn to a scale of 1:500 or 1: 1000. In case of very large compounds having more than one risk, it is advisable to submit separate plans for each risk with a key plan showing the relative situations of the various risks in the compound.

- SIGNS:

- Pucca walls to be shown by double lines, doors and windows being clearly marked.

- Perfect party walls to be indicated by the sign “T” at each end of the wall, or have the letters “P.P.W” along  side of across them at regular intervals and marked in distinctive colour.

- Fire proof doors and/or shutters to be marked as follows:

Single Fire Proof Door and/or Shutter   S.F.D

Double Fire Proof Door and/or shutter    D.F.D

- Sky lights to be marked “Sky Lights” or “S.L”

- INSTALLATION LAYOUT DRAWINGS:

- GENERAL

The scale shall be not less than 1:100. Layout drawing (dated) shall include the following information:

- north point indication;

- Constructional details of floors, ceiling, roofs, partition walls             and exterior walls.

- Sectional elevations of each floor of each building showing the distance of detectors from ceiling, structural features, humidification ducts, exhaust ducts etc., which affect the detector layout.

- the location and size of false ceiling/false floors, voids, offices and  other enclosures situated at a level lower than the roof or ceiling proper;

- Indication of  trunking,  platforms, machinery, fluorescent light fittings, heaters, etc. which may adversely affect layout of detectors;

- a key to the symbols used.

- type of detectors used.

- Various components associated with the system protection such as detectors, alarm panels, cables etc., shall be of a type and make, acceptable to the Tariff Advisory Committee and the drawings submitted shall be accompanied by full technical specifications for the same.

- No discounts will be considered for an alarm system unless the proposal for the same has been approved in advance by Committee and the system is fully inspected and tested by the Committee’s engineers and found in order.

- The prior submission of proposal to the Committee before the work is commenced, is essential, to ensure that the installation conforms to the Committee’s requirements. It does not however dispense with the procedure laid down hereafter re-application for the sanction of discounts.

- Application for discounts shall be submitted upon completion of the system, alongwith “as erected” drawings of the installation.

- No application for discount can be entertained until the relative appliances are complete, in position, ready for use and fully operative. An appropriate discount or allowance shall be sanctioned by the Committee from the date of receipt of the completed application, subject to the appliances being found in order on inspection by the Committee’s Inspectorate.  In the event of the installation being found incomplete or defective, the discount will be withheld until the defects have been rectified to the satisfaction of the Committee.

- No allowance shall be granted for Fire Alarm System until notified by the Committee either by letter or circular. It can be granted with effect only from the date specified in such notification.

- Insured are advised not to change block numbers as this affects the Committee’s   records and causes confusion. If block numbers are changed, the Committee shall be notified at once.

- COMMITTEE’S INSPECTION STAFF:

- The Committee undertakes, as far as possible a periodical inspection of all premises in which fire alarm appliances, entitling the risk to discounts for such appliances, are installed.

- For this purpose, the Committee’s inspecting engineers shall have the right of access to the premises of the Insured at any time with or without any prior notice.

- The primary duty of the engineers is to report to the Committee on the condition and efficiency of the appliances installed as well as to ensure that the regulations are being observed. They will, however, give help and advice in the maintenance of the appliances and on matters pertaining to fire protection and prevention.

- The attention of the engineers shall be drawn during their visits, to any change effected since earlier inspection or to any contemplated extension and alteration to the existing services. This procedure does not, however, dispense with the necessity of advising the Insurance Company of any changes, which affect the plan of the risk or the details of the appliances recorded with the Committee.

________________________________

RULES FOR FIRE ALARM SYSTEM

- ZONING OF FIRE ALARM SYSTEMS:

- GENERAL REQUIREMENTS:

- In most of the buildings an alarm of fire may initiate a number of different activities, e.g. provision of assistance, commencement of fire fighting operations and emergency evacuation procedures, summoning of fire brigade etc., It is essential that these activities are well co-ordinate. In the pre-planning of emergency procedures for a building it is therefore important, for ease of communication and synchronization of effort, to fix a convenient number of easily identifiable sectors/zones, which the building can be divided.

The detectors and manual call points within sectors/zones shall be wired to the Control and indicating equipment.

The entire electrical installation pertaining to the entire fire alarm system as described above shall be independent of other systems.

- When a signal of fire is given it is necessary that there should be no Confusion about the zone from which it is received.

To facilitate response by persons providing assistance, the zone should be small enough for a fire located quickly.

It is advisable to provide adequate fire separation between the zones.

- In larger premises, the fire alarm system shall be so designed and arranged that it is fully compatible with the emergency procedures and provides at some central or convenient point, or points, an indication of the zone from which an alarm has originated.

In the case of two stage alarms, clear and unambiguous signals should indicate the emergency procedure to be adopted throughout each zone.

- If the requirement of detectors or call points is less than 20 in any                                                        area, division of the area into zones is not necessary. Similarly, sectorization is not necessary if the number of zones is not very large.

- For larger systems covering more than one building it may be necessary to create sectors in addition to zones in order to restrict the number of zones from which alarms originate simultaneously or in succession.

- It is not always possible to provide definite guidelines regarding the requirements for the division of sectors etc., as stated above due to the fact that the configurations are not same for all risks. The division into zones and/or sectors should be decided based o careful consideration on the type of risk and accessibility   of zones in respect of main circulation routes and the main control and indicating equipment.

- In general, the signals used in different zones in the same premises should be the same unless the background noise in one or more zones is such as to require different sounders.

- The zoning arrangement for systems in multiple occupations shall take into account the fact that the premises may not all be occupied at the same time. No zone shall include areas in more than one occupancy.

- SIZE AND NUMBER OF ZONES (PROTECTED WITH DETECTORS)

- The floor area of a single zone shall not exceed 2000 m2.

- The search distance i.e. the distance that has to be travelled by a searcher inside the zone to determine visually the position of the fire, shall not exceed 30M.

Remote indicator lamps outside doors of rooms, cabins etc., within a zone may be useful, if doors are likely to be locked. Making an area easier to search, the use of remote indicator lamps reduce the need for a large number of smaller zones.

- If the total floor area of a building is 300 m2 or less, it may be considered   as a single zone even though there may be more than one storey.

- Where the total floor area of a building is greater than 300 m2, all zones shall be restricted to a single storey.

Note 1	If the total floor area of a fire compartment is 300 m2 or less, and if any communication with other fire compartments is only at the lowest level of the building, such fire compartment may be considered as a single 00.zone even though there may be more than one stories within it;

Note 2	If detectors and call points are fitted in stairwells, light wells, lift wells and other flue like structures extending beyond a floor but within one fire compartment, the volume of the well or shall may be considered as one separate zone.

Note 3	The total floor area is the combined total of the floor areas of all the storeys, not just the plan area of building.

- Where a special risk is present within a large protected area, e.g. a spray painting both in engineering workshop, and it is considered important to obtain rapid identification of fire in that risk, such special risk shall be deemed as a separate zone.

- Where a zone extends beyond a single compartment, the zone boundaries shall be the boundaries of the fire compartments.

Note 1	It is permissible to have two complete fire compartments in one zone, or two complete zones in one fire compartment.

Note 2	It is not permissible to have a zone, which extends into parts of two compartments, or a compartment, which extends into parts of two zones.

- If the arrangement of an area is complex and time is likely to be wested   in search for the fire, not withstanding any limits shown above, the area shall be further sub-divided into zones that are easier to search.

- SIZE AND NUMBER OF ZONES (PROTECTED WITH MANUAL CALL POINTS)

- In systems containing only manual call points, location of a fire is usually known to the person operating the call point. As it is often difficult to get information in time to the safety personnel, the restriction on the size and number of zones (rules under section 4.2 above) shall also apply to the systems protected with manual call points only.

Note:	In case of outdoor plants, open storage’s and tank farms, size of zones shall be decided in consultation with the Committee.

- To prevent misleading indication of the position of the fire, it is advisable that manual call points be indicated in the control equipment separately from the detectors in zones, which are protected, by both detectors and manual call points. Circuits for the detectors and the call points should be different.

- SOUND LEVEL:

Sounders for the alarm panels shall be suitably distributed throughout the protected risk to ensure that the alarm is heard anywhere in the protected installation. A minimum sound level of either 65 dB (A) or 5dB(A) above any other noise likely to persist (even for a short time) shall be required for the sounders.

+ + + +  + + + + +  + +

RULES FOR FIRE ALARM SYSTEM

- TYPES OF FIRE DETETORS, THEIR CHOICE AND MANUAL CALL POINTS:

- GENERAL INFORMATION:

- Fire detectors are designed to detect one or more of three characteristics of a fire i.e. smoke, heat or radiation (flame). No one type of detector is the most suitable for all applications and final choice is dependent on the individual circumstances. It is often useful to employ a combination of different types of detectors.

- Most fire detectors, are affected not only by the level of the detected phenomena but also by the behaviour of the phenomena with time. In some cases it is the rate of change of phenomena; in others it is the effect, e.g. delays in smoke entry or thermal lags.

- All fire detectors respond to some extent to phenomena other than fire leading to false alarm situations, which is discussed elsewhere in these rules.

- TYPES OF DETECTORS:

- HEAT DETECTORS:

There are two types of heat sensitive detectors. One is the  `point’ type of detector responding to the temperature of the gases in the immediate vicinity of a single point. The other is the `line’ type detector, which responds to the temperature of the gases in the vicinity of a line (not necessarily straight line). Line type detectors can be integrating or non-integrating.

In the integrating type the response to the temperature at one point on the line is modified by the temperature of the remainder of the line while in the non-integrating type the response to temperature at one point is independent of the temperatures at other points on the line.

In both types (point and line), there are two main subdivisions as stated below:

  - Fixed temperature (static) elements: These are designed to Operate when they reach a pre-selected threshold temperature.

- Rate of rise temperature elements: These are designed to operate when their temperature rises abnormally quickly.

The heat detectors must comply with IS: 2175. A combination of these two types of detectors is most ideal.

- SMOKE DETECTORS:

There are two commonly used detectors for detecting smoke:

- IONIZATION CHAMBER SMOKE DETECTORS: These are based on the principle that the electric current flowing between electrodes in an ionization chamber is reduced when smoke particles enter the chamber.

- OPTICAL TYPE SMOKE DETECTORS: These operate by detecting the scattering or absorption of light by smoke particles.

There are point type smoke detectors, which detect smoke at one position. These may be used on optical or ionization principles.

There are `aspirating’ smoke detectors I which air is taken from a number of positions to a central detector and there are `Beam’ type smoke detectors working on the principle of optical obscuration principle. Beam detectors are effectively line detectors since they can detect presence of smoke in only a small part of the beam.

There are some optical beam smoke detectors, which can sense thermal turbulence from a fire by detecting the refraction of the beam at the turbulent interfaces between hot and cold air.

The smoke detectors must comply with IS: 11360. It is ideal to use a combinations of smoke detectors with diddc3ferent operating principles for efficient detection and elimination of false alarms.

- FLAM DETECTORS:

Flame detectors detect ultra-violet and/or infrared radiation. Both types use radiation sensitive cells that `see’ the fire either directly or through built-in lenses or reflectors.

Infra red detectors are intended to respond to the flickering radiation emitted by the diffusion type of flame normally found in fires. Because of the presence of other infra red sources, such as the sun, if red flame detectors usually have some method of discriminating between fire and non-fire radiation; flicker sensing or the use of one or more infra red emission bands.

Ultra violet flame detectors detect the ultra violet radiation emitted by the flames and normally operate in a range of way lengths from 200nm to 260nm. Solar radiation in this range is absorbed by the high attitude ozone layer, and hence ultra violet detectors do not normally respond to sunlight.

Combination of infrared and ultra violet detectors operating on single or dual wavelengths are used for special applications.

Ember detectors operating in the infrared region are used to detect moving fires.

Spark detectors operating in infra red region are useful in ducts and similar concealed area applications.

- LINEAR HEAT SENSING CABLES:

Linear heat sensing can be broadly divided into two categories: Digital or Analogue, depending upon the principle by which the sensing cable registers a change in temperature.

Digital sensor consists of a two-core cable in which the conductors are separated by a heat sensitive insolent. When a specified temperature is reached, the cable insulation breaks down and an alarm is indicated. In the case of analogue sensor, cores are separated by a negative temperature co-efficient polymer whose resistance will reduce in proportion to the temperature increase.

These cable are used for detecting fire and overheating in certain specific occupancies-(a) Cable tunnels, trays and vaults, (b) Material conveyors, (c) Bulk storage multi-racked areas, (d) Rim seals of floating roof tanks storing hazardous chemicals  and (e) a few other special occupancies.

- CHOICE OF FIRE DETECTORS:

- GENERAL

Every fire alarm system is a compromise. It is possible to increase the sensitivity of detectors but that would probably increase the frequency of false alarms.

It is possible to reduce the losses by reducing the spacing between the detectors or using several types of detectors in the same area but these would increase the cost of the system

It is possible to increase the frequency of testing but this might lead to increased disturbances on the premises.

Since each type of detector has its own advantages and disadvantages, and no one type of detector is most suitable for all applications, the choice of a detector to be used for a particular application is always a compromise.

In any automatic detection system a detector has to discriminate between a fire and the normal environment existing within the building.

The system chosen shall have detectors that are suited to the conditions and that provide the earliest reliable warning.

Each type of detector responds at a different rate to different kinds of fire. With a slowly smoldering fire such as the initial stages of a  fire involving cardboard, a smoke detector would probably operate first. A fire that evolves heat rapidly and with very little smoke could operate a heat detector before a smoke detector could operate first.

In general, smoke detectors would give appreciably faster responses than heat detectors but may be liable o give false alarms.

A combination of various detectors is necessary. The likely fire behaviour of the contents of each part of the buildings, the processes taking place or planned and the design of the building shall be considered. The susceptibility of the contents to heat, smoke and water damage shall also be considered.

Heat and smoke detectors rely on transport or the products of combustion from the fire to detector by process of convection. These detectors therefore require presence of a structure like ceiling to get the combustion products directed on to them. In vie of this, heat and smoke detectors are most suitable for indoor applications. These detectors are unsuitable for outdoor applications.

Flame detectors are suited for outdoor application. They are especially suited to risks in which smoldering is unlikely e.f.  liquid  fuels.

Flames detectors within buildings/building are used to supplement heat and smoke detectors, particularly in high ceiling structures provided an unobstructed view is available for the detectors from the height.

The choice of the detectors may also be affected by the environmental conditions within the premises. In general, heat detectors have a greater resistance to adverse environmental conditions than other types.

Again the location of detectors e.g. those nearer to blowers, air conditioning ducts etc. make them insensitive for sometime resulting in belated or no detection.

- HEAT DETECTORS:

Heat detectors, in general, are less sensitive than smoke detectors. They are unlikely to respond to smouldering fires. They are not suitable for the protection of places where small fires can cause high losses e.g. computer rooms.

These are suitable for use in situations where sufficient heat is likely to be generated and damage caused by heat generated by fire contributed main hazards.

Heat detectors with rate of rise elements are more suitable where ambient temperatures are low or vary only slowly, while fixed temperature detectors are more suitable where the ambient temperature is likely to fluctuate rapidly over short periods.

- SMOKE DETECTORS:

Ionization type detectors are particularly sensitive to smoke containing small particles such as that produced in rapidly burning flaming fires, but may be less sensitive to the larger particles found in optically dense smoke which may be produced by smoldering materials.

Certain materials like PVC when over heated produce mainly larger particles to which ionization type detectors are less sensitive.

Optical detectors are sensitive to larger, optically active particles, found in optically dense smoke but are less sensitive to the small particles found in clean burning fires.

Smoke detectors cannot detect the products of combustion from clean burning liquids (such as alcohol), which do not produce smoke particles.

Optical detectors incorporating thermal turbulence detection are suitable for clean burning liquids.

- FLAME DETECTORS:

These are not suitable for detecting smouldering fires. These detectors, being dependent on the straight-line transmission of flame radiation, are the fastest detectors in comparison with conventional detectors. These are most suited to surveillance of open large areas, warehouses, yards, flammable liquid processing areas etc.  These detectors require a clear and uninterrupted line of sight.

- MANUAL CALL POINTS:

Manual call points must be clearly identifiable and simple to use without the need for instructions as to their method of operation. The method of operation of all the call points shall be identical unless there is a special need for differentiation.

If necessary a strike shall be provided adjacent to the call point to facilitate breaking of the frangible cover.

The delay between operation of a call point and the giving of general alarm shall not exceed 3 seconds.

The manual call points shall comply with IS: 2189, in all respects.

- OTHER TYPE OF DETECTORS:

Detection systems not covered specifically under these rules may be used subject to submission of all details with full particulars in advance to the Committee and their approval thereafter.

+ + + + + + + + + +

- SPACING AND SITING OF DETECTORS AND MANUAL CALL POINTS:

- GENERAL

A well laid out detection system can perhaps do nothing to reduce the incidence of fire but can certainly help to lessen the resultant loss by reducing the delay between ignition and the start of effective fire fighting.

Heat and smoke sensitive detectors depend on the convective movement of the combustion products from the fire to the detector.

The spacing and siting requirements for these detectors are based on the needs to restrict the time taken for movement of combustion products to ensure that these combustion products reach the detectors fitted in the ceiling in adequate concentration within a reasonable time lag.

- SPACING OF DETECTORS:

- For the open areas under flat horizontal ceilings, the horizontal distance from any point in the area to the detector (point type) shall not exceed 5.3M for heat detectors or 7.5 m for smoke detectors.

Incase of line type detectors, spacing of not more than 18 M between two projected beams and not more than half that spacing from an external wall parallel to the beam may be used.

Beam length shall not exceed maximum permitted by approving authority.

Incase of air sampling detectors, distance between detector and farthest fan shall not exceed 10Mtrs.

- The maximum allowable height of the compartment is 7M for the Purpose of rule 6.2.1 above.

In case the height of the compartment exceeds 7M, the following restrictions shall apply.

- SMOKE DETECTORS:

- UPTO 7 M HEIGHT - either ionization or optical detector or a combination of both depending on occupancy.

- ABOVE 7M BUT LESS THAN 10M HEIGHT- combination of  ionization and optical detectors in a ratio of 1:1 with spacing reduced to 5M.

- ABOVE 10M UPTO 25M HEIGHT- optical beam detectors or air sampling detectors.

- HEAT DETECTORS:

- UPTO 5M HEIGHT:  Fixed temperature  (static) element type detectors or combination detector having fixed and ROR elements, Grade 2or 3; preferably in the ratio 1:1

- ABOVE 5M UPTO 9M HEIGHT: Rate of rise cum fixed temperature (static) element type detectors with spacing reduced to 3.5M (Grade 1 only):

- MORE THAN 9M HEIGHT: Heat detectors at these heights are not acceptable.

Note: Grade 1,2 & 3 mentioned above are as perIS: 2189-1996.

- Where high air movement prevails in the protected blocks, the following additional provisions shall apply (excluding those for protection of false ceiling, false floor plenums and shafts) over the restrictions stated in rules 6.2.1 and 6.2.2 above.

| Air changes Per hour inside block | Multiplying factor for modified |  |
| --- | --- | --- |
|  | Spacing | (area coverage) |
| less than 7.5 | 1.00 | (1.00) |
| 8.5 | 0.95 | (0.91) |
| 10.0 | 0.91 | (0.83) |
| 12.0 | 0.83 | (0.70) |
| 15.0 | 0.74 | (0.55) |
| 20.0 | 0.64 | (0.40) |
| 30.0 | 0.50 | (0.25) |
| 60.0 | 0.38 | (0.15) |

Note: Air changes per hour is defined as:

60X volume per minute of air supply to the protected space/(Volume of protected space)

- Detectors shall not be located in the vicinity of supply air diffusers.  Minimum distance between the detector and the air inlets/diffusers shall be at least 1.5 m.

- Detectors shall be so mounted as to favour the air flow towards return air openings.

- The above provisions shall not disturb the normal population (count) of detectors, which is provided assuming that air-handling systems are off.

After designing the detector spacing, it shall be crosschecked to ensure that there is at least one smoke detector for every 100 m2 or one heat detector for every 50m2 of the compartment area.

- SPECIAL CONSIDERATIONS:

- Ceilings and Roofs:

Protection of ceiling and roofs shall conform to BS: 5839, Part-1.

- Corridors:

If the corridors are less than 5M wide, the distance between the detectors (see rule 6.2.3) may be increased by half the difference between the actual width and 5M. If the corridor is more than 5M in width, the same shall be treated as a normal compartment.

- Walls and Partitions:

- Detectors shall not be mounted within 500 mm of any walls or partitions.

- If a compartment is divided into sections by walls, partitions or storage racks, their height shall be such that the distance between the top of the latter ad the ceiling shall be greater than 450 mm.

If the height difference is less than 300 mm, each section shall be deemed as separate room for provision of detectors.

- Obstructions:

- Any ceiling obstruction (such as beam, duct etc.,), the depth of which is more than 150mm the distance between the detectors (see rule 6.2.3) in the vicinity of such obstruction shall be decreased by twice the depth of obstruction.

However if the depth of obstruction is more than 10% of the ceiling height, such obstruction shall be treated as a wall and provision of detectors shall be governed by rule 6.2.4.3 above.

- Detectors shall not be mounted within 500mm of obstructions. However, in case of minor obstructions like light fittings etc., the distance may be reduced to 250mm.

- Voids and False-Floors:

All voids and false-floors having height of more than 800mm shall be provided with detectors and such detectors shall be installed within 150mm of the ceiling of such voids or false floors.

- Enclosed Staircases, Vertical Shafts and Ceiling Penetrations:

Where stairways, enclosed chutes or shafts or lifts, hoists or escalators penetrate ceiling/floors, detectors shall be sited at each level within 1.5M of the penetrations. In case of stairways not penetrating through the ceiling, detectors shall be provided at each of the landings.

- The Committee reserves its rights to insist on additional detectors wherever considered necessary depending upon the site of the detector installation to take care of adverse effects of stratification, surrounding environment, construction features etc.

- Where there are more enclosures or cabins per floors, false floors, false Ceilings, plenums and shafts, response indicators should be provided at permanent places.

- SPECIAL REQUIREMENTS:

- Where the atmosphere inside a block is subject to sudden or rapid changes in temperatures e.g. kitchen, boiler house etc., ROR type of heat detectors should be avoided to minimise false alarms.

- Where ambient temperatures are likely to be high, the operating temperatures of the heat detector should be at least 30 degrees C above the maximum anticipated ambient temperature.

- Toilets, WC blocks Bathrooms etc. need not be provided with detectors even when they from a part of the protected areas unless they are of more 2 M2 in area.

- A detector shall be placed within 1.5Mfrom any door, window or other openings in the wall partitions between protected and non-protected premises.

- Every enclosure like a cabin, however small it is, within the   protected compartment shall be provided with detector(s).

- Reference shall be made to the Committee in advance with full Particulars in following cases:

- Installation of smoke detectors within ventilation ducts;

- Siting of optical beam type smoke detectors having transmitter and receiver components;

- Layout of detectors in compartments where heating arrangements are provided (stratification of smoke).

- For areas which are subject to adverse environmental Conditions like vibration, pollution, shock etc.

- SITING OF MANUAL CALL POINTS:

- Manual call points shall be so located that, to give an alarm, no person in the premises has to travel distance of more than 30 m to reach them.

Where necessary, the travel distance may require to be reduced to less than 30M e.g. where there is difficulty in free access within the risk or in potentially dangerous risks.

- Call points shall be fixed at a height of 1.4M above the surrounding Floor level, at easily accessible, well-illuminated and conspicuous positions, which are free of obstructions.

- Where the call points are not visible from the front as in the case of a Long corridor, they shall be surface mounted or semi-recessed in order to present a side profile area of not less than 750 mm.

Manual call points shall be housed in dust proof and moisture proof    enclosure properly sealed with rubber lining.

The glass surface should be minimum 30 cm2 in area and glass thickness should not exceed 12mm.

- Approval of the Committee must be obtained before commencing the Installation for their specific requirements if any.

- Manual call point shall be located preferably near entry to staircases at various levels.

- SITING OF FLAME DETECTORS:

- GENERAL

- The location and spacing of the detectors shall be based on sound engineering evaluations taking into account the following:

- size of the fire requiring detection,

- fuel involved,

- sensitivity of detectors,

- distance between the fire and detector,

- radiant energy absorption of the atmosphere,

- presence of other sources of emission and

- purpose of detection system.

- Certain   flame detectors respond to the instantaneous level of radiation received while others depend upon the level received over a period.

In either case the response will depend on the distance between the flame detector and the fire, since the radiation level received is inversely proportional to the square of this distance. Increased distance from the fire will, therefore, lead to an increase in the size of the fire at detection.

- A clear line of sight to the area being protected is of great   importance but at the same time care must be exercised to avoid a direct line of sight to likely sources of non-fire radiation to prevent false alarms.

- SPACING GUIDE-LINE:

- Sufficient  no.  of  detectors shall be used and they shall be

Positioned such that no point requiring detection in the hazard area is obstructed or outside the field of view of at least one detector.

- In applications where, the fire to be detected could occur in         an area not on the optical axis of the detector, the distance        shall be reduced or alternatively more detectors added to      compensate for the anguladis placement of the fire.

- The spacing of the detectors shall vary from fuel to fuel. It               is therefore necessary to fix the distances as per the recommendations of the manufacturers.

- The location of the detectors shall also be such that structural members or any other opaque objects or materials do not impede their line of sight.

- When installed outdoors, detectors shall be shielded to prevent diminishing sensitivity due to rain, snow, ice etc., and allow a clear vision of the hazard area.

- Approval of the Committee must be obtained before commencing the installation for their specific requirements.

- SITING OF MISCELLANEOUS DETECTORS:

- SPECIAL SPRINKLERS:

For the spacing of sprinklers particularly those of types like thermo electric, pre-action etc. reference shall be made to the Committee’s rules for Sprinkler Installation

- CABLE GALLERIES:

- Each cable tray shall be protected by LSHS cable unless the vertical distance between the trays is uniformly less than 500 mm in which case alternate trays (in addition to the top and bottom trays) shall be protected.

- The LSHS cable shall be laid on the cables at the centre Line of the cable-runs either straight along the cables or zigzag and back and forth across the ladder and trays.

- It is also possible to suspend the LSHS cables below the trays so as to be within 200 mm of the cable-runs at a pitch of 1.2 M like a catenary.

- Where the width of the tray exceeds 1M, two LSHS cables shall be laid on the trays as above. Alternatively, cables maybe laid in an zigzag fashion in which case pitch of the zigzag profile shall not exceed 1.2 mtrs.

- It is always necessary to install two LSHS cables below                     the lower most tray because accumulation of filth, rubbish                     and waste in such areas is a distinct possibility rendering                    them fire-prone.

- Approval of the Committee must be obtained before commencing the installation for their specific requirements.

- BELT CONVEYORS:

- The following fire situations are considered for the protection of the conveyors with LSHS cables.

a) Stationery conveyor, b) Moving conveyor, c) Belt                                                            Roller friction, d) Belt friction with adjoining portions                                                            of the structures, e) Spill of fuel, lubricants and the                                                             like on the return belt).

The LSHS cables can be considered for detection of                                                             any one combination of two or more of the situations                                                            described above.

- The method of mounting the LSHS cables under the above circumstances depends upon convenience of mounting as well as the vulnerability of the LSHS cables.

The LSHS cables shall be mounted as close to the Risks mentioned above as possible i.e. on both sides of the belt rollers, or above the material carrying belt on separate supports or combination of both depending on the circumstances.

- Approval of the Committee shall be obtained before commencing the installation for their specific requirements if any.

- For other types of risks to be detected by the installation                 Of LSHS cables, Committee shall be approached in advance with full particulars.

- Every fire detector should be allotted an identification number                          Preceded by alphabetical initials showing the type of                        detector from the time of inspection prior to commissioning.

+ + + +  + +  + + +

- CONTROL AND INDICATING EQUIPMENT;

- GENERAL:

Control and indicating equipment comprise components for the reception, indication, control and relay signals originating from detectors or calls points connected to it., for  the activation of  alarm sounders and alarm sign alling devices.

The equipment shall be available for zones, sectors and the main control area as the case may be.

- LOCATION:

The control equipment has two important functions. It is the point from which the systems are controlled and the point at which the system indications are given. Various considerations are therefore associated in respect of location of the equipment as below:

- ACCESSIBILITY TO THE STAFF:

The members of staff on duty will be the first to require information given by equipment, indicating the zone affected. Location of the equipment shall therefore be such that many people are likely to be around at any given time.

- AVAILABILITY TO THE FIRE FIGHTING STAFF:

The equipment shall preferably be located in ground floor                                                          or near the entrance points which are used by fire fighting  staff or fire  brigade.

If multiple entries are likely to be used repeater panels are necessary near such entrances.

- LIGHTING LEVEL:

The ambient light level in the vicinity of the equipment shall be such that the indications from the  panels are clearly visible.  Wherever necessary additional lighting should be provided, the supply for which must be taken from the alarm circuits.

- SOUND LEVEL:

The sound level in the vicinity shall be such that the audible indications from the panel are distinctly heard.

A minimum sound level of either 65 DB (A) or 5 DB (A) above any other noise likely to persist (even for a short time) shall be required for the sounders.

- FIRE PRONE AREAS:

The equipment shall be so situated that they are unlikely to be involved in a fire before adequate warning is given. If the system uses automatic detectors then the area in which C&I equipment is cited should also be covered by detection system.

- MULTIPLE OCCUPANCY RISKS:

The location of the equipment shall be in a mutually agreed common area so that all the occupants have access to the indicating equipment.

- ENVIRONMENTAL FACTORS:

Where the equipment is situated outdoors or in severe environments (within or outside a building) care shall be taken to protect the equipment from the adverse surroundings.

- INDICATION OF ORIGIN OF ALARMS:

- PURPOSE:

Except in buildings where a fire can be located without delay, the fire alarm system shall indicate  the origin of  alarm. The indications shall be such that they can be easily, quickly and unambiguously related to the position in the building from which the alarm has originated. The indications shall be clear both to staff who may have to assist in evacuation or fire fighting and to the external fire brigade.

- INDICATIONS

The primary indication of the origin of alarm shall be an indication of the zone of origin.

In very large installations, a graded series of displays maybe required, with a central indicator panel specifying the sector of origin, and a further panel within the sector to show the zone origin.

Except in small premises, the display giving only the identification of individual detectors may be difficult to interpret; and could lead to difficulties in assessing the spread of fire or the occurrence of secondary fires. Such a display, if provided, shall be subsidiary to the main zonal display.

- METHOD OF INDICATION

Many variations are possible in the method of indication depending upon different situations and the size of the installation. Rapid location of the fire within the premises must be possible.

Where one compartment split into several zones, the indication should preferably show the absence of fire separation between the zones.

The indications in the  panel can be through display of letter and/or numbers or permanent mimic diagram and/or Video Display Units or a combination of the above.

- POWER SUPPLY:

The power required for the display shall be derived from the fire alarm panel itself and power requirements for all sector and zonal panels shall be derived from the main control panel.

All these loads shall be considered at the time of design with a view  to arrive at the power requirement for the alarm system at the initial  stages.

- SECTOR AND ZONAL PANELS AND C & I EQUIPMENT:

The requirements for the sector/zonal panels and also the control and indicating equipment shall be governed by relevant provisions under IS-2189.

The provisions shall include	 requirements of audio-visual alarm signals, fault signals, DC voltmeter, alarm sounders, MCPs etc.

The main panel as well as sector/zonal panels shall have certification of specified authorities as per the testing Clauses of IS-2189.

RULES FOR FIRE ALARM SYSTEM

- POWER SUPPLY CABLING AND WIRING AND CONTROL CENTRE:

- POWER SUPPLY:

- The System Shall Derive Its Power From Either-

- the main electricity supply (normal supply) or

- the stand by power supply that shall be  immediately available in the event of failure of normal supply which shall be automatically connected so as to maintain the equipment in ready condition of taking the maximum load.

The stand by supply shall be derived normally from exclusive storage batteries OR UPS of adequate capacity. Alternatively captive power generation with a provision of AMF (Automatic Mains Failure) control panel or continuous power generation can be accepted as stand   by power supply.

- The C & I equipment shall be connected to the mains through an exclusive circuit with protective gears, e.g. switch fuse MCB etc. reserved solely for the purpose, its cover being painted red and labelled `FIRE ALARM’-DONOT SWITCH OFF’.

- The minimum capacity of the normal mains supply shall be calculated so as to meet the total power consumption of the entire system in quiescent condition plus that of all the sounders with at least 25 percent zones in alarm condition.

- Main connection to the system shall be arranged such that the mains supply to the system (which should be through exclusive protecting gear) is not interrupted as a result of switching off mains power to premises (other services).

- The stand by power supply shall be capable of maintaining the system in normal operation for a period of not less than 48 hours after the failure of mains supply. Simultaneously it should guarantee operation of detectors in at least 25 percent of zones (with a minimum of two zones) and the operation of the fault indicator. The operation of trigger devices in further zones must not result in cancellation of fire alarms existing at that time.

Note:   Where failure of normal mains supply is not likely to be made good within 24 hours due to long unattended/unoccupied periods, the system inspection frequency need to be arranged at such intervals that in the event of normal mains supply failure, at least 24 hours stand by capacity remains at the time of next inspection.

- Stand by power supply derived from exclusive back-up batteries shall have provision of automatic load switch-over (whenever normal mains supply fails) and automatic charging.

It shall be insured that charging conditions are matched to the system. The rate of battery charging shall be such that, having discharged to its final voltage, the battery can comply with the requirements of rule 8.1.5 after a charging period 24 hours.

- The voltage of the batteries shall be monitored and low                         Voltage must be indicated on C & I equipment.

- CABLING, WIRING OF FIRE ALARM PANELS:

- The cables shall conform to the following:

- PVC insulated copper conductor cables con forming to IS:694-1977 having minimum 1 mm2 cross-sectional area, (If stranded cables with at least 0.5 mm2 cross section shall be used).

- Rubber insulated braided cables conforming to IS:9968 (Part I)-1981.

- Armoured PVC/rubber insulated cables conforming to IS:1554(Part I)-1976.

- The cables shall be used exclusively for the detection      system.  The multicore cable shall not be shared for other low voltage or high voltage circuits.

Cables/ wiring must be completely encased in rigid metallic PVC conduits.

- Cables connected to detectors shall be given `S’ loop on both sides of the detectors which shall be properly clamped to the ceiling.

`S’ Loop shall also be left where cables connect    sounders, panels, dampers, etc.

Appropriated glands shall be provided for the armored cable near terminals of junction box.

Unused cable holes if any should be plugged.

- All the cables and wires shall be tagged for proper identification.

Wires shall be identified by ferrules at junction and cables by colour  bands at every 3 m distance.

- Over –hear lines for fire alarm system shall not be used when connecting different building. They shall be laid under ground according to IS: 1255-1983.

- The cables and wiring for fire alarm circuit shall not be clubbed with other cables and wiring which must be laid well away  from them.

- The panel should have additional capacity to operate auxiliary equipment like fire dampers, ventilation and/or pressurizing fans, emergency light, smoke vents etc., if required.

- CONTROL CENTER:

- In high rise buildings and special buildings like mercantile, Hotels, Educational, assembly etc., a control center of an area of 16m2 to 20m2 shall be provided where the control and indicating equipment power supply units and other fire protection ancillary panels could be installed.

This shall preferably be o ground floor.

- The control center room shall have. Emergency lighting   system.

- The control centre room shall have intercom and direct telephone facilities.

Where possible, a direct hot line to local fire brigade shall be provided.

- The control center room shall have mimic panel of the premises protected showing details of all the fire protection systems. Fire orders shall be prominently displayed.

- Control center in air-conditioned premises shall be segregated from the rest of the building, preferably with an independent air-conditioning system.

- In industries or buildings where fire and security functions are combined, the fire control centre room shall be separated from the security office area by a wall having glass panel.

+++++++

- INSPECTION, INITIAL TESTING AND COMMISSIONING:

- GENERAL:

Even a well designed and properly installed automatic fire alarm system will not be able to render reliable and trouble-free service unless high standards of maintenance and supervision are ensured during the entire service period of the system.

Regular inspections and scheduled preventive maintenance are critical and shall include all the components of the system.

- INITIAL INSTALLATION INSPECTION TESTS:

- After installation, a visual inspection of all the detectors shall be made to make sure that they are properly sited.

Each detector shall be inspected to ensure that it is properly mounted and connected.

- Restorable heat detectors and restorable elements of combination detectors must be tested by a heat source, such as a hair dryer, or a shielded heat lamp until it responds, making sure that the sensing element is not damaged.

After each heat test, the detector shall be reset. Precautions shall be taken to avoid damage of the non-restorable element of a fixed temperature or a combination rate of rise/fixed temperature detector.

- Non- reset table fixed temperature heat detectors, which are not to be heat-tested, shall be tested mechanically or electrically for fire alarm function.

- Heat detectors with replaceable fusible alloy element shall be tested first by removing the element to see whether contacts operate properly and then by re-inserting them in proper position.

- In periodic testing, heat detectors shall be visually examined for damage or other conditions such as heavy coats of paints, etc. likely to interfere with their correct operation.

- Each smoke detector shall be tested to initiate an alarm at its installed location with smoke or other approved aerosol, which demonstrates that the smoke can enter the chamber and initiate an alarm.

- In order to ensure that each smoke detector is within its sensitivity range, it shall be tested using either.

- a calibrated test method, or

- a manufacturer’s/supplier’s approved calibrated sensitivity  test instrument, or

- approved control equipment arranged forth purpose, or

- other approved calibrated sensitivity test method.

Note: Detector’s sensitivity cannot be tested or measured using any spray/smoke-producing device that administers an unmeasured concentration of aerosol/smoke into the detector.

- Detectors found to have sensitivity outside the approved range shall be replaced.

- SERVICING AND MAINTENANCE:

- To ensure that regular and reliable servicing/maintenance of the systems and its components is carried out, any of the following methods shall be adopted:

- An agreement/contract with competent contractor who shall attend to the maintenance/repair, when necessary, promptly.

Servicing arrangement must be made immediately on completion of the installation irrespective of whether the premises are occupied or not. If the premises are not occupied, special precautions shall be taken, if necessary, to protect the system against damage by dampness of other causes.

- Where no such service contract is entered into at least one qualified employee of the user with suitable experience of electrical equipment must under go special training to deal with all aspects of basic servicing and maintenance, including routine  sensitivity   tests/checks of the detectors, as and when required.

- For institutional occupancies, such as hospitals, hotels etc. an engineer shall be on call at all times and that request over the telephone for emergency service shall be executed promptly I any case, within 24 hours.

- MAINTENANCE SCHEDULE:

- It is the responsibility of the user of the equipment to ensure that proper instructions are obtained from the manufacturer/supplier or installer regarding the routine attention and test procedures.

- The routine to be adopted in individual premises may vary with the type of occupancy of the premises.

Equipment installed in corrosive or dirty environmental conditions will need to be checked more thoroughly and at more frequent intervals than that in clear and dry situations.  Care shall be taken that all equipment are properly reinstated after testing.

The occupants of the premises shall be notified of any test of the system that may result in the sounders being operated.

- Daily attention by the User:-A check shall be made every day to ascertain that:

- The panel indicated normal operation.

- If not, any fault indicated is recorded in the log book and is receiving urgent attention, and

- Any fault warning recorded the previous day has received attention.

- WEEKLY ATTENTION BY THE USER:

The following tests shall be made every week to ensure that the system is capable of operating under alarm conditions:

- Once a week, at least one trigger device on one zone circuit shall be operated to test the ability of the control and indicating equipment to receive a signal and to sound the alarm and operate other warning devices.

If there is more than one zone on a system having unmonitored wiring each unmonitored zone shall be tested each week, but without sounding the alarm more than once.

For systems   having monitored wiring and up to 13 zones, each zone shall be tested in turn but if there are more than 13 zones, more than one zone may need to be tested in a week such that the interval between tests one   zone does not exceed 13 weeks.

It is preferable that each time a particular zone is tested, a different trigger device is used. An entry shall be made in the log  book quoting the particular trigger device that has been used to initiate the test.

If the operation of the alarm sounders and/or the transmission of the alarm signal has been prevented by disconnection, then a further test shall be carried out to prove the final reinstatement of the sounders, and if permissible, the alarm transmission circuits.

- A visual examination of the battery and connections shall be made to ensure that they are in good conditions. Action shall be taken to remedy any defect, including low electrolyte level.

Any defect shall be recorded in the logbook, reported to the responsible person, and action taken to correct it.

- QUARTER INSPECTION AND TEST BY THE USER:

The following checklist and test sequence is recommended.

- Entries in the log book since the previous inspection shall be checked for actions taken.

- Batteries and their connections shall be examined and tested to ensure that they are in good serviceable condition.

- Where provided, secondary batteries shall be examined to ensure that the specific gravity of electrolyte in each cell is correct. Necessary remedial action must be taken and an appropriate entry made in the logbook.

Contamination of electrolyte can ruin a cell.

Care shall be taken to ensure that hydrometers, vessels, etc. used in the servicing of alkaline secondary cells are not contaminated by acid and vice-versa.

- Primary batteries, including reserves, shall be tested to varify that they are satisfactory for a further period.

- The alarm functions of control and indicating         equipment shall be checked by the operation of a trigger device in each zone as described.

The operation of alarm sounders and any  link to a remote manned  centre shall be tested.

All ancillary functions of the control panel shall also be tested where practicable.

All fault indicators and their circuits shall be checked preferably by simulation of fault conditions.

The control and indicating equipment shall be visually inspected for signs of moisture ingress and other deterioration.

- A visual inspection shall be made to ensure that structural or occupancy changes have not affected the requirements for re-siting of trigger devices, manual call points, smoke detectors and heat detectors.

The visual inspection must also confirm that a clear space of at least 750mm radius is preserved in all directions below every detector, the detectors are properly sited and that all manual call points remain unobstructed and conspicuous.

Any defect shall be recorded in the logbook reported to the responsible person, and action taken to correct it.

    - Annual Inspection Tests:

The following checks and test sequence shall be carried out:

- The instruction and test routines details in 10.4.5 (a),(b),(c),(d),(e) and (f) must be followed.

- Operation of at least 20 percent of the detectors in an installation shall be checked each year, and the selection shall be done in such a way that all the detectors I an installation shall have been checked once in every 5 years for replacement by new ones.

- Each detector shall be checked for correct operation using specified test equipment and method, except non- reset-able   detectors.

The checks to be carried out are specified in 9.2.2 to 9.2.6 in respect of heat detectors and, 9.2.7 in respect of smoke detectors.

- Visual inspection shall be made to confirm that all cable fittings and equipment are secure, undamaged and adequately protected.

- At least once every three years, at the annual inspection, the electrical installation shall be tested.

Any defect shall be recorded in logbook and suitable remedial action taken.

- On completion of the annual inspection entry shall be made in register in respect of defects found. After the defects are rectified, the entries shall again be made.

  - GENERAL POINTS ABOUT DETECTORS:

It is essential to ensure specified range of sensitivity of the detectors being installed. Sensitivity range shall be checked on equipment as specified.

It is essential to apply frequent sensitivity checks and routine tests as prescribed in the rules so that the correct sensitivity levels/degree is maintained during the entire service span of the installation.(see rule 9.2.7).

  - CLEANING AND MAINTENANCE: -

Detectors require periodic cleaning to remove dust or dirt accumulated. The frequency of cleaning depends on the type of detector and the local ambient conditions. In any case, the interval shall not exceed a period of 3 months, for each detector.

The cleaning, checking, operating and sensitivity adjustment shall be attempted only after referring manufacturers’ instructions.

These instructions shall details methods such as creating vacuum to remove loose dust and insects or washing heavy greasy and grimy deposits, following partial disassembly or the washing of detectors to remove contamination.

  - TESTS FOLLOWING AN ALARM OR FIRE:

All detectors suspected of exposure to a fire condition shall be tested in accordance with the provisions contained in these rules pertaining to annual inspection tests.

In addition, a visual check of the battery charger shall be carried out to ensure perfect serviceability. A check shall be made of the extent of damage, if any, to the cables and other components and also the operation thereof.

  - SYSTEM DISCONNECTION DURING TESTING:

Care shall be taken to minimize the disruption of the normal use of the building by alarm sounding during detector testing.

If detectors are removed for testing or servicing, replacement detectors shall be provided.

  - SPARES: -

It is necessary to keep spares in premises like covers for manual call points, fuses, spare detectors and other essential spares based on the size of the installation.