- INTRODUCTION

A sprinkler system consists of a water supply (or supplies) and one or more sprinkler installations; each installation consists of a set of installation control valves and a pipe array fitted with sprinkler heads. The sprinkler heads are fitted at specified locations at the roof or ceiling, and where necessary between racks, below shelves, inside ovens or stoves or below obstructions. The main elements of a typical installation are shown in the figure 1.

A sprinkler has two functions to perform. It must first detect a fire, and must then provide an adequate distribution of water to control or extinguish it. Each function is performed separately and one is independent of the other except insofar as early detection makes extinction easier because the fire has not grown large. The classic use of the sprinkler is in the hot gas layer which forms beneath the ceiling of an enclosure in which a fire is developing.

The sprinklers operate at pre-determined temperatures to discharge water over the affected part of the area below, the flow of water through the alarm valve initiating a fire alarm. The operating temperature is generally selected to suit ambient temperature conditions. Only sprinklers in the vicinity of the fire, i.e. those which become sufficiently heated, operate.  It should not be assumed that the provision of sprinkler system entirely obviates the need for other means of fighting fires and it is important to consider the fire precautions in the premises as a whole.

Structural fire resistance, escape routes, fire alarm systems, particular hazards needing other fire protection methods, provision of hose reels and fire hydrants and portable fire extinguishers, etc., safe working and good handling methods, management supervision and good housekeeping all need consideration. It is essential that sprinkler systems should be properly maintained to ensure operation when required. This routine is reliable to be overlooked or given insufficient attention by supervisors. It is, however, neglected at peril to the lives of the occupants of the premises at the risk of cripple financial loss. the importance of proper maintenance cannot be too highly emphasized. When sprinkler systems are disabled, extra attention should be paid to fire precautions and the appropriate authorities informed. This has been discussed in detail in sections 18 and 19 of the regulations.

The regulations have been divided into 20 sections and each section deals elaborately with various aspects of the sprinkler protection system. The pipe sizing and hydraulic calculations for various hazards are discussed in detail.  Figures have been shown for several rules where more clarity is required. The rules are clearer about where the system is not required and where the systems can be excluded.

Grading of the sprinkler system has been revised more realistically. The pumping capacity and the water requirements for the sprinkler system have been clearly defined. The changes made from the 30th edition of the sprinkler rules have not in anyway diluted the protection requirements. The changes have been made to suit the Indian conditions.

- DEFINITIONS

For the purpose of this part of regulations, the following definitions shall apply:

- Alarm test valve.  A valve through which water may be drawn to test the operation of the water motor firm alarm and/or of any associated electric fire alarm.

- Alarm valve. A check valve, of the wet, dry or composite type, that also initiates the water motor fire alarm when the sprinkler installation operates.

- Alarm valve, pre-action.  An alarm valve suitable for a pre-action installation.

- Alarm valve, re-cycling.  An alarm valve suitable for a recycling installation.

- Alarm valve, wet.  An alarm valve suitable for a wet installation.

- Arm pipe.  A pipe, other than the last section of a range pipe, feeding a single sprinkler.

- Assumed maximum area of operation, hydraulically most favourable location. The location in a sprinkler array of an AMAO of specified shape at which the water flow is the maximum for a specific pressure.

- Assumed maximum area of operation, hydraulically most unfavourable location.  The location in a sprinkler array of an AMAO of specified shape at which the water supply pressure is the maximum needed to give the specified design density.

- Cut-off sprinkler.   A sprinkler protecting a door or window between two areas only one of which is protected by the sprinkler.

- Design density.   The minimum density of discharge, in mm/min of water, for which a sprinkler installation is designed, determined from the discharge of a specified group of sprinklers, in L/min, divided by the area covered, in M2.

- Design point.  A point on a distribution pipe of a pre- calculated installation, downstream of which pipe work is sized from tables and upstream of which pipework is sized by hydraulic calculation.

- Distribution pipe.  A pipe feeding either a range pipe directly or a single sprinkler on a non-terminal range pipe more than 300 mm long.

- Distribution pipe spur.  A distribution pipe from a main distribution pipe, to a terminal branched pipe array.

- Drencher.  A sprayer used to distribute water over a surface to provide protection against fire exposure.

- Drop.   A vertical pipe feeding a distribution or range pipe.

- End-side array.   A pipe array with range pipes on one side only of a distribution pipe. (see Figures 2 and 3)

- End-centre array. A pipe with range pipes on both sides of a distribution pipe. (see Figures 4 and 5)

- Fastener. A device for attaching pipe hanger components to a building structure or racking.

- Fire door.  A door and frame of specified fire resistance complying with either : Building regulations published by TAC, or BS 476: Part 8: 1972; or BS 476: Part 22: 1987 with respect to integrity.

- Fire resistance.  The ability of a component or the construction of a building to satisfy for a stated period of time the appropriate criteria specified in the relevant part of BS 476.

- Fire shutter.  A shutter and frame of specified fire resistance complying with either: Building regulations published by TAC, or BS 476: Part 8: 1972; or BS 476: Part 22: 1987 with respect to integrity.

- Fully hydraulically calculated.  A term applied to pipework sized as specified in 18. (a) or an installation in which all the pipework downstream of the main installation control valve set is sized as specified in 18.1(a)

- Hanger.  An assembly for suspending pipework from the elements of building structure.

- High-rise system.  A sprinkler system in which the highest sprinkler is more than 45M above the lowest sprinkler or the sprinkler pumps whichever is the lower.

- Hydraulic alarm, intermittent.  Sounding of an hydraulic water motor alarm gong for intervals totalling less than the alarm period.

- Installation sprinkler installation. Part of a sprinkler system comprising a set of installation main control valves, the associated downstream pipes and sprinklers.

- Installation, pre-action.   A dry installation in which the alarm valve can be opened by an independent fire detection system in the protected area.

- Installation, re-cycling.  A pre-action installation in which the alarm valve can be opened and closed repeatedly by a heat detection system.

- Installation, wet pipe.  An installation in which the pipe work is always charged with water.

- Jockey pump.  A small pump used to replenish minor water loss to avoid starting an automatic suction or booster pump unnecessarily.

- Low-rise system.  A sprinkler system in which the highest sprinkler is not more than 45M above ground level or the sprinkler pumps.

- Main distribution pipe.  A pipe feeding a distribution pipe.

- Node. A point in pipe work at which pressure and flow(s) are calculated; each node is a datum point for the purpose of hydraulic calculations in the installation.

- Precalculated.  A term applied to pipe work sized as specified in 18,1(b) or an installation in which pipe downstream of the design point are sized as specified in 18.1(b).

- Range pipe.  A pipe feeding sprinkler directly or via arm pipes of restricted length.

- Riser.  A vertical pipe feeding a distribution or range pipe above.

- Rosette sprinkler rosette.  A plate covering the gap between shank or the body of a sprinkler projecting through a suspended ceiling, and the ceiling.

- Section.  The part (which may be one or more zones) of an installation on a particular floor fed by a particular riser.

- Sling rod.  A rod with a sling eye or screwed ends for supporting pipe clips, rings, band hangers etc.,

- Sprinkler, ceiling or flush  pattern.   A pendent sprinkler for fitting partly above but with the temperature sensitive element below, the lower plane of the ceiling.

- Sprinkler concealed.  A recessed sprinkler with a cover plate that disengages when the heat is applied.

- Sprinkler conventional pattern.  A sprinkler that gives a spherical pattern of water discharge.

- Sprinkler glass bulb.  A sprinkler which opens when a liquid filled glass bulb bursts.

- Sprinkler horizontal.  A sprinkler in which the nozzle directs the water horizontally.

- Sprinkler Intermediate.  A sprinkler installed below, and additional to the roof or ceiling sprinklers.

- Sprinkler, pendent.  A sprinkler in which  the nozzle directs water downwards.

- Sprinkler, roof or ceiling.  A sprinkler protecting the roof or ceiling.

- Sprinkler sidewall pattern.  A sprinkler that gives a downward paraboloid pattern discharge.

- Sprinkler upright.  A sprinkler in which the nozzle directs the water upwards.

- Sprinkler system.  The entire means of providing sprinkler protection in the premises comprising one or more sprinkler installation, the pipe work to the installations and the water supply /supplies except  town mains and bodies of water such as lakes or canals.

- Sprinkler yoke arms.  The part of the sprinkler that retains the heat sensitive elements in load bearing contact with the sprinkler head valve.

- Staggered sprinkler lay out.  An off-set lay out with the sprinklers displaced one half pitch along the range pipe relative to the next range or ranges.

- Standard sprinkler lay out.  A rectilinear lay out with the sprinkler aligned perpendicular to the run of the ranges.

- Suction pump.  An automatic pump supplying water to a sprinkler system from a suction tank.

- Suitable for sprinkler use.  A term applied to equipment or component accepted by the authorities as far a particular application in a sprinkler system either by a particular system or by compliance with specified general criteria.

- Supply pipe.  A pipe connecting a water supply to a trunk main or the installation main control valve set(s); or a pipe supplying water to a private reservoir, suction tank or gravity tank.

- Suspended open cell ceiling.  A ceiling of regular open cell construction through which water from sprinkler can be discharged freely.

- Terminal main configuration.  A pipe array with only one water supply route to each range pipe.

- Terminal range configuration.  A pipe array with only one water supply route from a distribution pipe.

- Toggle support.  A swivel device for securing hangers to hollow sections ceiling or roofs,

- Trunk mains.  A pipe connection to two or more water supply pipes to the installation main control valve set(s).

- User.  The person responsible for or having effective control over the fire safety provision adopted in or appropriate to the premises or the building.

+ + + + + + + + +  +

# REQUIREMENTS REGARDING SUBMISSION OF PLANS

  - Plans for submission to the Committee shall be drawn up in accordance with the following requirements;

- Plans shall be clear, contain all required details including scale and point of Compass and shall be dated.

- Plans of new installation shall show the entire compound; all buildings therein, with their door and window openings, and the boundary walls. Buildings under construction and future extension envisaged shall be indicated by the dotted lines. Plans of extensions to approved existing installations need not show the rest of the compound but sufficient details shall be given of the existing installations in correlation to the extension, to enable the Committee's Inspection staff to check the plans and offer comments. In case of storeyed buildings, drawings submitted shall include plans of each storey together with sectional elevations.

- Material: Plans shall be on White paper or ammonia paper or Ferro Prussiate paper.

- Plans shall generally be prepared in accordance with IS: 696, shall not exceed 850 x 1200 mm in size and shall be drawn to a scale of 1: 500 or 1: 1000. In the case of very large compounds with more than one risk, it is advisable to submit separate plans for each risk with a key plan showing the relative situation of the various risks etc., in the compound.

  - SIGNS:

- Pucca walls to be shown by double lines, doors and windows being clearly marked. (Figure 6)

- Iron or other non-masonry walls to be shown by a thin line and nature of construction indicated. (Figure 7)

- Perfect party walls to be indicated by the sign "T" at each end of the wall, or have the letters ‘PPW’ alongside or across them at regular intervals and marked in distinctive colours. (Figure 8)

- Fireproof doors and/or shutters to be marked as follows:

Single Fireproof Door and/or Shutter    -     ‘SFD’

Double Fireproof Door and/or shutter  -     ‘DFD’

- Skylights to be marked "Sky Lights" or "SL"

- Boiler to be shown by a rectangular figure marked "Boiler".

- Sprinkler mains to be shown by a blue line; the diameter, length and number of pipes being marked alongside and specials and reducers to be clearly indicated as below.

- m.m dia, lengths of -metre each (Figure 9)

- Sprinkler pumps to be clearly marked and the capacity and head to be indicated in each case.

- Pump(s) suction piping to be shown dotted and diameter to be indicated. (Figure 10)

- Fire service water tanks and reservoirs to be shown to scale. (Figure 11)

- Sprinkler trunk mains to be shown by a blue line, the sizes being marked alongside.

____________________________

mm dia Spk main

- Fire alarm bells to be shown by a blue line, the sizes being marked  "F.A.B."

- Sprinklered blocks to be marked "S".

- Electric cable(s) for the fire pump(s) to be shown in green line(s).

- PROCEDURE TO BE FOLLOWED IN THE CASE OF APPLICATION FOR DISCOUNTS

The sanction of discounts off insurance premiums shall necessarily follow consideration by the Regional offices of TAC of all details of the risk, of manufacturing processes involved and the protective appliances to be installed in order to ensure that the standards laid down have been fully observed.  To prevent confusion or disappointment, definite rules for procedure have been laid down as follows:

- Proposals for the installation of appliances shall be submitted to the Regional offices of TAC Committee by the Leading Office on the risk and shall comprise-

- Material specifications of equipment and components of the installation, indicating the name of manufacturers and Indian Standards Specifications, if any

- In the case of internal appliances, details of the areas of the various compartments, their occupation and the quantities and types of appliances proposed.

- In the case of sprinkler and hydrant installations, fully dimensioned plans in duplicate as called for in Section.1 shall be submitted.

- In addition to the above, the following details would be necessary in the case of Sprinkler installation:

  - Drawings showing layout of the entire sprinkler system, incorporating    material specifications, different sizes of mains etc.,

### In case of storeyed blocks, floor area of each floor showing particulars.

- Layout of pump house showing clearly the suction, delivery and priming (if any) and freeboard arrangements.

- Details of water storage tanks giving particulars of compartmentation and jackwell, details of inflow and particulars of tappings for other purposes, if any.

- Sub-station location in relation to other blocks if the pump is electrically driven.

- Plans of Sub-station showing thickness of internal walls and equipment layout. Also walls between transformers if outdoor and located within 6M or specified distance according to oil contents as specified in rule 6.1.6 of the committee's electrical regulations.

- Route of cable from Sub-station to fire pump house.

- Schematic circuit line diagram showing electric feed to fire pump.

- the number of sprinklers on each installation control valve set;

- the height of highest sprinkler on each installation control valve set;

- the type(s) of installation(s) and the nominal diameter(s) of the main control valves;

- the number or reference of each installation main control valve set;

- a statement that the system will comply with this specification including details of any deviation(s) from its recommendations with reasons for the deviation(s).

- a list of the components suitable for sprinkler use, included in the system each identified by manufacturer's name and model/reference number.

  - INSTALLATION LAYOUT DRAWINGS

- General.  The scale shall be not less than 1: 100. Layout drawing shall include the following information:

  - north point indication;

  - the class or classes of installation according to hazard class including stock category and design storage height;

  - constructional details of floors, ceiling, roofs and exterior walls and walls separating sprinklered and non-sprinklered areas;

  - sectional elevations of each floor of each building showing the distance of sprinklered from ceiling, structural features, etc., which affect the sprinkler layout or the water distribution from the sprinklers;

  - the location and size of concealed roof or ceiling voids, offices and other enclosures sealed at a level lower than the roof of ceiling proper;

  - indication of trunking, staging, platforms, machinery, fluorescent light fittings, heaters, suspended open cell ceilings etc., which may adversely affect the sprinkler distribution;

  - the sprinkler types(s) and temperature ratings(s);

  - the location and type of main control valves and location of alarm motors and gongs;

  - the location and details of any water flow and air or water pressure, alarm switches;

  - the location and size of any tail-end air valves, subsidiary stop valves and drain valves;

  - the drainage slope of the pipework;

  - the location and specification of any orifice plate;

  - a schedule listing the numbers of sprinklers, medium and high-velocity sprayers etc., and the area of protection;

  - a key to the symbols used.

- PRE-CALCULATED PIPEWORK. For pre-calculated pipework the following details shall be given on, or with, the drawings;

  - identification of the design points of each array on the layout drawing;

  - a summary of the pressure losses between the control valve and the design points at the following design rates or flow.

1) In a light-hazard installation 225 L/min, 2) In an ordinary-hazard installation: 1000 L/min and 3) In a high hazard installation the flow corresponding to the appropriate design density.

- For light and ordinary-hazard installations with pre-calculated pipework the pressure needed at the design point is not stated. Instead the friction loss in the pipework between the control valve and the design points is limited to a predetermined quantity, incorporated in the value specified for pressure at the control valves.  Static head is added to this pressure to give the value defining the minimum actual water supply running pressure. A typical summary of pressure losses is shown at the end of this section. (Figure 12)

- HYDRAULICALLY CALCULATED PIPEWORK. For hydraulically calcu-lated pipe work, the following shall be given, with detailed calculations, either or purpose designed work sheets or as a computer print-out:

  - for each design area of operation:

    - the area identification;

    - the hazard class;

    - the specified density of discharge (in mm/min);

    - the assumed area of maximum operation (AMAO) (in m2);

    - the number of sprinklers in the AMAO;

    - the sprinkler nominal orifice size (in mm);

    - the maximum area covered per sprinkler (in m2);

    - detailed and dimensioned working drawings showing the following:

(i) the node or pipe reference scheme used to identify pipes, junctions, sprinkler heads and fittings which need hydraulic consideration; (ii) the position of the hydraulically most favourable AMAO.  (iii) the position of the hydraulically most unfavourable AMAO.   (iv) the four sprinklers upon which the design density is based.    (v) the height above datum of each point of identified pressure value.

  - for each operating sprinkler:

    - the sprinkler node or reference number;

    - the sprinkler nominal  k factor;

    - the flow through the sprinkler ( in L/min);

    - the inlet pressure to the sprinkler or sprinkler assembly (in bar);

  - for each hydraulically significant pipe;

    - the pipe node or other reference;

    - the pipe nominal bore ( in mm);

    - the hazen-williams constant (c or k factor)  for the pipe.

    - the flow through pipe ( in L/min);

    - the nominal fluid velocity ( in m/sec);

    - the length of pipe ( in m);

    - the numbers, types and equivalent lengths of fittings;

    - the static head change in pipe (in m);

    - the pressures at inlet and outlet of pipe in bar;

    - the friction loss in pipe ( in bar)

    - the indication of flow direction.

Note: - A line diagram of the pipe layout should be prepared showing the following:

- the node or pipe reference numbers;

- the distribution pipes;

- the range pipes;

- the sprinkler heads under consideration;

- the four hydraulically most unfavourably placed heads.

- the flow through, and pressure at the end of each hydraulically

- significant pipe.

- WATER SUPPLY DRAWINGS.   The drawings shall show water supplies and pipework therefrom up to the installation control valves. The drawings shall be on an indicated scale of not less than 1:100. A key to the symbols shall be included. The position and type of stop and check valves and any pressure reducing valve, water meter, water lock, orifice plate and any connection supplying water for other services shall be indicated.

- HYDRAULIC CALCULATION.

- Pre-calculated installations.

An hydraulic calculation (with relevant flow tests) shall show that each trunk main together with any branch main, from each water supply to a main installation control valve set water supply test and drain valve and control valve 'C' gauge (i.e., including the installation control valves) is capable of providing the required pressure and flow at the installation control valve test and drain valve.

- Fully hydraulically calculated installations.

Where the pipework is fully hydraulically calculated the following additional details shall be given:

- a modified pressure-flow characteristic graph indicating the usable pressure at any flow up to the maximum installation demand:

- the demand pressure-flow characteristic graph for each installation for the hydraulically most unfavourable (and if required the most favourable) AMAO with pressure taken as at the control valve 'C' pressure gauge.

  - Discounts will be considered only if all the equipment associated with the system protection such as pumps, engines, motors, valves, sprinklers, installation valves, hand appliance and their accessories  are of a type and make, acceptable to the Tariff Advisory Committee.

  - No discounts will be considered for a sprinkler system unless the same has been hydraulically tested with trenches open (in case of underground mains) at least twice during the course of installation by the Committee's engineers and found in order.

  - The prior submission of proposal to the Committee before the work is commenced, is essential, to ensure that the installation will conform to the Committee's requirements but does not dispense with the procedure laid down hereafter for application for the sanction of discounts.

  - Application for discounts shall be submitted on special forms provided for the purpose by the Committee and shall comprise :

(a) Application by the Leading Office (Appendix I),  (b) Guarantee by the Insured (Appendix II) and  (c) Schedule of Appliances (Signed by the Insured) (Appendix III) [see section 19]

  - In every case, a plan of the premises prepared in accordance with the requirements indicated in rule 3.1 shall accompany any application for a discount for fire extinguishing appliances and, in the case of sprinkler and/or hydrant installations, Installing Engineer's detailed "As Erected" working drawings are essential.

NB: A certificate of Completion from the installing Engineers' stating that pressure tests to which the installation(s) has been subjected and giving the date(s) from which it was in complete working order may also be submitted.

  - Even in the case of extensions to an existing service, a complete set of forms and plans detailed above shall be submitted.

  - No applicant for discount can be entertained until the relative appliances are complete, in position, ready for use and fully operative.  An appropriate discount or allowance will be sanctioned by the Committee from the date of the completed application, ( in accordance with the rules above) subject to the appliances being found in order on inspection by the Committee's Inspectorate.  In the event of the installation being found incomplete or defective, the discount will be withheld (or withdrawn if already notified) until the defects  have been rectified to the satisfaction of the Committee.

  - No allowance shall be made for Fire Extinguishing Appliances until notified by the Committee either by letter or circular, and then, with effect only from the date specified in such notification.

  - Insurer and the insured are advised not to change block numbers as this naturally affects the Committee's records and causes confusion. If block numbers have to be changed, the Committee shall be notified at once.

- COMMITTEES INSPECTION STAFF

- The Committee undertakes, as far as possible a periodical inspection of all premises in which fire extinguishing appliances, entitling the risk to special discounts or ratings for such appliances, are installed.

- For this purpose, the Committee's inspecting engineers shall have the right of access to the premises of the Insured at any time with or without giving any prior notice.

- The primary duty of the engineers is to report to the Committee on the condition and efficiency of the appliances installed as well as ensure the regulations are being observed.  They will, however, give help and advice in the maintenance of the appliances and on matters pertaining to fire protection and prevention.

- The attention of the engineers shall be drawn, during their visits, to any change effected since the previous inspection or to any contemplated extension and alteration to the existing services. This procedure does not, however, dispense with the necessity of advising the Insurance Company or Companies interested on the risk of any change which affect the plan of the risks or the details of the appliances recorded with the Committee.

- CLASSIFICATION OF OCCUPANCIES

  - As the water supply, pumping capacity and other features of the sprinkler installations depends not only on the size of the risk, but also on its fire growth and spread potentialities, the risks are to be categorized under the following classes for the purpose of design of the installation.

Light hazard class,

Ordinary hazard class,

High hazard class.

Storage hazards.

  - The list provided hereunder under each class is not very exhaustive.  For categorisation of any risk not listed, reference to the committee with full particulars is essential prior to the design of the installation.

Typical occupancies are as shown below:

    - LIGHT HAZARD CLASS:

Non-industrial occupancies where the areas of rooms, corridors, halls etc. are not more than 125 m2 and above are bounded by masonry/or R.C.C. walls raised up to the roof and door openings therein protected by doors.

Typical occupancies are as follows:

Hospitals

Hotels

Institutions

Libraries

Laundries

Museums

Nursing homes

Office buildings

Prisons

Schools, Colleges etc.,

- It any occupancy or block within the Light hazard risk is larger than 125 m2 in area or having an area less than 125 m2 in area but not bound on all sides as stipulated above, the risk shall be classified as 'ordinary' hazard.

- ORDINARY HAZARD (Manufacturing occupancies)

- Abattoirs Abrasive wheel and powder

- Aircraft factories (excluding hangers)

- Airport terminal buildings

- Bakeries

- Biscuit factories, Book-binders, Publishers

- Breweries

- Boot and shoe units

- Cables

- Candle

- Cardboard factories

- Carpentry and furniture [not involving foam/ foam plastics]

- Carpets

- Car parking areas within building or basement

- Cement

- Ceramics

- Chemicals

- Cinematographic and TV Produc-tion / broadcasting studios

- Cloth processors

- Confectioneries Dairies

- Dehydrated vegetable factories

- Departmental stores/Retail shops

- Electronic equipment and assembly

- Engineering workshops

- Fibreboard factories

- Flax, Jute and hemp mills

- Flour Mills

- Food and beverages

- Glass factories

- Hosiery and garment

- Jewellery

- Laboratories

- Motor garages

- Paint shops

- Paper mills

- Photographic film factories

- Plywood factories

- Printing presses Restaurants and cafes

- Rope factories

- Rubber and Plastics (other than foam plastics)

- Soap factories

- Sugar Mills

- Synthetic fibres/yarn factories

- Tanneries

- Textile mills

- Timber and wood-working (except saw mills)

- Theatres

- Tobacco factories

- Wood wool

- Woollen mills

- Vermicelli

- Wax factories

- HIGH HAZARD (Manufacturing occupancies)

- Aircraft hangers

- Bitumen and wax coated paper

- Celluloid goods Cellulose Nitrate

- Cigarette Filter

- Distilleries

- Duplicating/stencil paper Explosives

- Fire works

- Floor cloth and Linoleum

- Foam plastics and foam rubber

- Hessian cloth/Tar felt Match factories Oil mills

- Paint, Colour and Varnish factories

- Resin, Rosine, Turpentine and lamp black

- Rubber substitutes making units

- Saw mills

- Surgical cotton, Mattress  and Pillow makers

- Tar distillation units

- Woodwool manufacturers

- STORAGE OCCUPANCIES

Storage risks (stacked or high-piled) are categorised under four classes as per classifications below:

CATEGORY-I

Carpets, Non-synthetic/synthetic yarn and fabrics, Mechanical and electrical goods (dominantly metal parts) and hardware items,  Glassware and Crockery, Fibreboard, groceries, metal goods, Papers other than those listed under categories 2 and 3 below, Powdered and canned foods, Plastic/glass bottles containing non-flammable liquids etc.,

CATEGORY-II

Batteries, Baled Cotton/synthetic fibres, Books, Baled cork, Baled waste paper, Cartons containing alcohols (in cans/bottles), Cartons of canned lacquers which dry by solvent evaporation, Chipboard, Cardboardrolls (horizontallystored), Cereals/Grains/Foodstuff/Flour/ Sugar in sacks, Cellulose/Cellulose pulp, Electrical goods other than those stated in Category-I, Flammable liquids in non-combustible containers, Leather goods, Palletised liquor stocks, Plastics (non-foamed, other than cellulose nitrate), Rolled pulp and paper and asphalted paper (Horizontal storage), Veneer sheets, Wooden patterns, Metal/wooden furnitures with plastic seats etc.,

CATEGORY-III

Bitumen/Wax coated paper, Candles, Carbon black, Card board rolls (vertically stored), Charcoal, Coal, cellulose nitrate, Foamed plastic and foam rubber products, Flammable liquids in combustible containers, Linoleum products, Matches, Plastics other than those stated in Category II, Rolled pulp and paper and asphalted paper (vertical storage), Rubber goods including tyres and tubes, Sawn timber,  Ventilated wood stacks, Waxed and asphalt coated papers and containers in cartons, Wood wool, wooden pallets and flats(idle), All materials having wrappings or pre-formed containers of foamed plastics etc.,

CATEGORY-IV

Off-cuts and random pieces of foamed plastic or foamed rubber rolls of sheets of foamed plastic or foamed rubber, Foam mattress, Expanded polystyrene packaging, Foam upholstery etc.,

+ + + +  + + + + +  +

- PLANNING

- INITIAL CONSIDERATIONS

  - CONSULTATION

Where a sprinkler system or an extension or alteration to a sprinkler system is being considered for new or existing building the committee shall be consulted at an early stage:

- OUTLINE DESIGN

Consideration should be given to any benefits that might be gained by changes in building design, work procedures etc., when preparing the outline design.   In planning site layout and building design, particular consideration should be given to the following: -

- the occupancy hazard class and goods category which determine  the water discharge density and water supply pressure and flow :

- the siting of any main water supply connection(s);

- the siting of any water supply tank(s) or reservoir;

- the siting of any pump house;

- the maximum quantity of water available from the supply source compared with the system requirements;

- the location of sprinkler installation control valves, together with the access thereto, indication of their position, and the disposal of drainage and water supply test water;

- the source and means of supply of electric power, etc.

- the protection of valve sets, pipework and sprinklers against accidental damage.

- It is important to consider building design in the context of fire protection, e.g. choice of materials, support of sprinkler pipework having regard to the load imposed on structure by the weight of sprinkler pipework and the contained water, need for inbuilt drainage (which is strongly advised for computer areas) or raising of base of stacked goods above the floor where water damage may be severe etc., when storage of goods is involved it may be appropriate to consider the height of the building and of material stacks, and the height and type of any storage rack which may have a considerable bearing on fire protection costs. The design of double entry storage racks may be influenced by the need to mount sprinklers therein. Where sprinklers are fitted in racks additional rack structural members may be needed to prevent impact damage to the sprinkler head and pipe work.

- INTERACTION WITH OTHER FIRE PROTECTION MEASURES.

Account shall be taken of possible interaction between sprinkler systems and other fire protection measures.  Examples of possible adverse interactions between sprinkler protection and other fire protection measures are :

- water damage to an inadequately shielded fire alarm control panel in a sprinkler protected area with consequent possible failure of the fire alarm system.

- Operation or failure of smoke detectors in zones adjacent to one in which water discharge is taken place because of the water spray mist travelling to adjacent zones.

Such possible interactions need careful considerations.

- EXTENT OF SPRINKLER PROTECTION;

- BUILDING TO BE SPRINKLER-PROTECTED

The sprinkler system shall provide protection to all parts not specified as exceptions (in rule 5.2.2) in one of the following:

- the building under consideration;

- any building communicating directly or indirectly with the building under consideration.

Where there are unprotected buildings within 6 M of protected building the exposure hazard can be reduced by using cut-off sprinklers over unsealed openings and drenchers over combustible walls in the protected building.

- EXCEPTIONS (BUILDINGS AND PARTS OF BUILDINGS NOT SPRINKLER-PROTECTED)

Obligatory exceptions, sprinkler protection shall not be provided in the following parts of a building or plant:

- grain silos or grain bins inside buildings forming part of corn mill, distillery, maltings or oil mills;

- Ovens, hovels and kilns in pottery, earthenware, brick, tile and glass works;

- areas, rooms or places  where the water discharged from a sprinkler may pose a hazard.

Sprinklers should not be fitted over salt baths, metal melt pans or frying ranges, or in positions where water may discharge into them or indirectly drain into them nor should water pipes be fitted in these positions.

- OPTIONAL EXCEPTIONS

Generally sprinkler-protection shall be considered for, but need not be provided in, the following parts of a building or plant:

- Stairs, spaces below stair headings (but not rooms above a stair)  and lift wells. Any part not provided with sprinkler protection shall be separated by walls (225mm brick or 100mm R.C.C) as per Building regulations. Fire doors not less than 1hr in fire resistance, shall be provided in the openings of such walls.

- Washrooms, toilets and WCs (but not cloakrooms). Any part not provided with sprinkler protection shall be separated by walls (225mm brick or 100mm R.C.C) as  per Building regulations. Fire doors not less than 1hr in fire resistance, shall be provided in the openings of such walls.

- Rooms or compartments containing electric power distribution apparatus, such as switchgear and transformers, and used for no other purpose(s). Any part not provided with sprinkler protection shall be separated by walls (225mm brick or 100mm R.C.C) as per Building regulations. Fire doors not less than 1hr in fire resistance, shall be provided in the openings of such walls.

- in papermaking machines, the undersides of screens or of shields erected over the wet and (where there is no other fire hazard);

- COMMUNICATING BUILDINGS.    Sprinkler protection shall be considered for, but need not be provided in, the following communicating buildings or structures:

- a building or storey segregated from the sprinklered building by walls of not less than 4h fire resistance in which each opening is protected by two (arranged in series) fire doors or fire shutters each of not less than 2h fire resistance;

- canopies of non-combustible construction, not extending beyond 2.3 m from the building wall. Any such canopy not provided with sprinkler protection shall be fitted with cut-off sprinklers under the canopy over each opening between it and the spinklered building. Any opening 2.5m or less in width shall be provided with a cut-off sprinkler, positioned centrally over the opening. Openings exceeding 2.5m in width shall be provided with cut- off sprinklers over the opening, not more than 2.5m apart and with a sprinkler not more than 1.25m, from each side.

- exterior loading docks and platforms either of the non-combustible construction or with the space beneath closed off against accumulation of debris;

- Building used solely as offices and/or private dwelling(s). Any part not provided with sprinkler protection shall be separated by walls (225mm brick or 100mm R.C.C) as per Building regulations.  Fire doors not less than 1h in fire resistance, shall be provided in the openings of such walls along with cut-off sprinklers.

- stairs, washrooms and WCs external to the sprinkler- protected building, in which all openings to the sprinkler-protected building are protected by doors of not less than 1h fire resistance or cut-off sprinklers.

- staircases, washrooms, toilets and WCs external or internal to the sprinkler-protected building which form a means of communication between the sprinklered building and non-sprinklered building. In any such part not provided with sprinkler protection all openings into the communicating area from the sprinklered and from the non-sprinklered building shall be protected by fire doors of not less than 2h fire resistance.

- STORAGE IN OPEN OR OPEN SIDED SHED

The distance between combustible materials stored in the open or in an open-sided shed and the sprinklered building shall be no less than 10M or 1.5 times the height of the stored material whichever is greater unless there is a fire wall in between or a suitable drencher system to protect the openings of the protected building facing the open storage.

+ + +  + + + +  + + + +

- GRADING OF SPRINKLER INSTALLATIONS

Sprinkler systems are graded according to the type of the installation.  There are three grades:

GRADE 1

- Systems protected by two automatic pumps, one of which shall have a compression-ignition engine drive, each capable of providing independently duty conditions as specified in rule 9.1.4 of this manual. (In other words, there shall be primary pump(s) and standby pump(s) of identical capacity(ies) and prime movers of both shall be of different types)

- Where two completely independent electrical power sources are available (neither linked with the other), or where automatic changeover facilities exist between two   entirely   independent electrical power sources, provision of two electrically driven pumps can be considered.

- The total number of sprinklers in the installation (excluding those in the concealed spaces) of the protected building or range of   buildings does not exceed 2000; with not more than 200 sprinklers   (excluding   those in the concealed spaces) in each separate risk.

A separate risk is defined as a detached building or one separated from the other adjoining buildings by perfect party walls as per Committees rules for segregation.

GRADE 2

Systems as described in Grade 1 but without any limitation as to the number of sprinklers stated in item "b" above.

GRADE 3

Systems protected by pumping capacity(ies) as per rule 9.1.4 of this manual.

+ + + + + + + + + + +

- WATER SUPPLY.

- Water for the sprinkler system shall be stored in any easily accessible surface or underground reservoir or above ground tanks of steel, concrete or masonry. The effective capacity of the reservoir (above the level of foot valve seat by a height equivalent to three times the diameter of the suction pipe in case of negative suction and above the level of suction puddle flange or the level of top of the pump casing whichever is higher by a height equivalent to three times the diameter of the suction pipe in case of positive suction) for various classes of occupancies of sprinkler installations shall be as indicated in Table 1 hereunder:

TABLE - 1

| CLASS OF HAZARD | EXCLUSIVE WATER STORAGE |
| --- | --- |
| LIGHT HAZARD | Not less than 20 minutes run for the pumping capacity or 35 m3 whichever is greater |
| ORDINARY HAZARD | Not less than 1 hour run for the aggregate pumping capacity or 200 m3 whichever is greater. |
| HIGH HAZARD | Not less than 2 hours run for the aggregate pumping capacity. |

- A higher capacity of reservoir than that required as per Table 1 may be stipulated by the Committee where considered necessary.

- Water supplies for the sprinkler installations shall be free from suspended, fibrous or other matters, which may accumulate in the system pipework, and it is recommended to use filtered water for the system.

- The use of salt or brackish water is not normally allowed. In special circumstances where there is no suitable fresh water source available, consideration may be given for the use of salt or brackish water provided the installation is normally charged with fresh water.

- Combined reservoirs for other fire fighting systems such as Hydrant system, Water spray systems etc., along with the sprinkler system are permissible provided a) All the suction inlets or foot valves are at same level and   b) Aggregate capacity of the reservoir is equal to the total requirement of all the systems put together.

- Reservoirs of and over 225-m3 capacities shall be in two independent but interconnected compartments with a common sump to facilitate cleaning and repairs.  The construction and arrangement of the reservoir and the common sump shall be in accordance with the provisions in rule 7.3 of the Fire Protection Manual (12th edition) published by the Committee.

- Level indicator shall be provided for measuring the quantity of water stored at anytime. The indicator shall preferably be graduated to read directly in M3 of water.

- Water reservoir shall be cleaned at least once in two years or more frequently if necessary to prevent contamination and sedimentation.

- It is advisable to provide adequate inflow into the reservoir so that the protection can be re-established within a short period.

+ + + + + + +  +

- DESIGN DENSITY AND AMAO FOR FULLY HYDRAULICALLY CALCULATED OR PRE-CALCULATED SPRINKLER SYSTEMS.

- The design density and the assumed maximum area of operation for various types of risks are as specified below and also see Table 2.

- LIGHT HAZARD:  The density of water discharge shall be at least 2.25 lpm/m2 over an assumed area of operation covering 84 m2

Not more than six sprinklers shall be installed in a room except in either a corridor where there is a single line of sprinklers or a concealed space protected as specified in 12.3.1(a).

- ORDINARY HAZARD: The density of water discharge shall be at least 5 lpm/m2 over an assumed area of operation covering 360 m2

- HIGH HAZARD: The density of water discharge for process risks shall be at least 10 lpm/m2 over an assumed area of operation covering 260 m2

TABLE - 2

MINIMUM DESIGN DENSITY AND AMAO FOR LIGHT, ORDINARY AND

HIGH HAZARD (PROCESS) RISKS AT ROOF/CEILING SPRINKLERS

| HAZARD | DESIGN DENSITY lpm/m2 | AMAO m2 |
| --- | --- | --- |
| Light Ordinary High | 2.25 5.00 10.00 | 84 360 260 |

- STORAGE HAZARDS:

- Storage hazards are categorised from the nature and type of storage. When the height of storage increases beyond specified limits, fire fighting is rendered more difficult. In worst cases it may not be possible to fight the fire due to difficulties in reaching the seat of fire and also accessibility to the fire fighting staff is impaired due to excessive smoke. In case of the sprinklers also the same difficulties are encountered. Storage risks can be categorised under "ordinary" or "high" depending upon the type and method of storage of goods within the godown/warehouse blocks

- The storage occupancies can be regarded as "ordinary hazard" risks if the height of storage is within the limits for various categories as shown below.

TABLE - 3

| CATEGORY | MAXIMUM STORAGE HEIGHT IN METRES | DESIGN DENSITY LPM/M2 | AMAO M2 |
| --- | --- | --- | --- |
| I | 4.00 | 5 | 360 |
| II | 3.00 | 5 | 360 |
| III | 2.00 | 5 | 360 |
| IV | 1.25 | 5 | 360 |

In other words, goods stored not higher than what is stated in Table 3 below for the appropriate category  or not higher than the eaves height of the roofs or within 1M of a flat ceiling whichever is the lowest shall be regarded as Ordinary hazard storage.  If the above conditions are not met, the risk shall be regarded as high hazard storage.

- In case of high hazard storage risks, the nature of the hazard is determined by the height of storage, storage aisle width and area of each storage block. In other words, goods stored not higher than what is stated in Table 4 below for the appropriate category  or not higher than the eaves height of the roofs or within 1M of a flat ceiling whichever is the lowest shall be regarded as high hazard storage.

- REQUIREMENTS COMMON TO ORDINARY AND HIGH HAZARD STORAGE RISKS:

- Wherever possible, the deflector of the sprinkler fitted in the ceiling shall be at more than 1.5M from the goods stored below.  However, in case of Jute godowns, no jute stock shall reach within 2M of the deflectors of the sprinkler heads.

- In case of storage in racks or shelves, if the height of storage is more than what is specified in Tables 3 and 4, intermediate sprinklers shall be provided for each shelf/rack in addition to the ceiling sprinklers and overall design density and AMAO shall be maintained as per the Table 3 or Table 4.

TABLE - 4

| CATEGORY | MAXIMUM STORAGE HEIGHT IN METRES | DESIGN DENSITY lpm/m2 | AMAO m2 |
| --- | --- | --- | --- |
| I | 6.5 | 12.50 | 260 |
| II | 5.5 | 15.00 | 260 |
| III | 4.5 | 17.50 | 300 |
| IV | 3.5 | 22.50 | 300 |

- If the top of the storage in the top tiers of the racks or shelves is within 3 M of the roof sprinklers, top tiers need not be protected by the intermediate sprinklers. However, the other tiers shall need to be sprinklered.

- The aisle width between the storage stacks shall not be less than 2.5 meters and the maximum area of each storage stack shall not be more than 150 m2.  If these parameters are exceeded, the design density applicable shall be loaded by 2.5 LPM/M2 .

- For storage heights beyond what is stated in rule 8.1.4.3 above, the basis for design is rendered invalidated and in such cases full details of the risk shall be submitted to the committee in advance for consideration.

- In case of mixed storage (both ordinary and high hazard storage) in buildings, the parameters will be governed by the most hazardous occupancy.

- PRESSURE AND FLOW REQUIREMENTS.

- LIGHT HAZARD: For the design density and the AMAO specified the water supply running pressure at the installation valve shall not be less than 2.2 bars plus the static pressure equivalent of the height of the highest sprinkler in the installation above the "C" gauge when a water is being discharged at a flow rate of 225 LPM.

- Ordinary hazard:  For the design density and the AMAO specified, the water supply running pressure at the installation valve shall not be less than 2 bars plus the static pressure equivalent of the height of the highest sprinkler in the installation above the "C" gauge when water is being discharged at a flow rate of 1800 LPM or 1.5 bars plus the static pressure equivalent as stated above when the flow rate is 2100 LPM.

- HIGH HAZARD:

- The design density, flow rate and pressure requirements for different floor areas for this hazard class are as per the Tables 5, 6, 7 and 8 below:

# TABLE – 5

| Pressure and Flow requirements for high hazard installations with 15mm (K=80) sprinklers pre-calculated and pipe sizes from Tables 23 and 25. |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Minimum Design Density (lpm/m2) | Flow rate past installation valve (lpm) | Running pressure at the design point at the level of the highest sprinkler in the high hazard area (bars) |  |  |  |  |  |  |
|  |  | Floor area per sprinkler in m2 |  |  |  |  |  |  |
|  |  | 6 | 7 | 8 | 9 | 10 | 11* | 12* |
| 10.0 | 2800 | 1.8 | 2.4 | 3.2 | 3.9 | 4.8 | 5.8 | 6.8 |
| 12.5 | 4550 | 2.7 | 3.7 | 4.8 | 6.0 | 7.3 |  |  |
| 15.0 | 4550 | 3.8 | 5.2 | 6.8 |  |  |  |  |

*When an Ordinary hazard installation requires to be upgraded to high hazard, these parameters shall be used.

## TABLE - 6

| Pressure and Flow requirements for high hazard installations with 15mm (K=80) sprinklers pre-calculated and pipe sizes from Tables 24 and 26 |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Minimum Design Density (lpm/m2) | Flow rate past installation valve (lpm) | Running pressure at the design point at the level of the highest sprinkler in the high hazard area (bars) |  |  |  |  |  |  |
|  |  | Floor area per sprinkler in m2 |  |  |  |  |  |  |
|  |  | 6 | 7 | 8 | 9 | 10 | 11* | 12* |
| 10.0 | 2800 | 1.3 | 1.8 | 2.4 | 3.0 | 3.8 | 4.6 | 5.5 |
| 12.5 | 4550 | 2.0 | 2.8 | 3.6 | 4.6 | 5.7 | 7.0 | 8.4 |
| 15.0 | 4550 | 2.8 | 3.9 | 5.1 | 6.5 |  |  |  |

*When an Ordinary hazard installation requires to be upgraded to high hazard, these parameters shall be used.

TABLE - 7

| Pressure and Flow requirements for high hazard installations with 15mm (K=80) sprinklers pre-calculated and pipe sizes from Tables 24 |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Minimum Design Density (lpm/m2) | Flow rate past installation valve (lpm) | Running pressure at the design point at the level of the highest sprinkler in the high hazard area (bars) |  |  |  |  |  |  |
|  |  | Floor area per sprinkler in m2 |  |  |  |  |  |  |
|  |  | 6 | 7 | 8 | 9 | 10 | 11* | 12* |
| 10.0 | 2800 | 0.7 | 1.0 | 1.3 | 1.6 | 2.0 | 2.4 | 2.8 |
| 12.5 | 4550 | 1.1 | 1.5 | 2.0 | 2.5 | 3.0 | 3.7 | 4.4 |
| 15.0 | 4550 | 1.6 | 2.2 | 2.8 | 3.6 | 4.4 | 5.3 | 6.3 |
| 17.5 | 4550 | 2.2 | 2.9 | 3.8 | 4.8 | 5.9 | 7.2 |  |
| 20.0 | 5600 | 2.8 | 3.8 | 5.0 | 6.3 | 7.8 |  |  |
| 22.5 | 5600 | 3.5 | 4.8 | 6.3 | 8.0 |  |  |  |
| 25.0 | 6750 | 4.4 | 5.9 | 7.8 |  |  |  |  |
| 27.5 | 6750 | 5.3 | 7.2 |  |  |  |  |  |
| 30.0 | 9000 | 6.2 |  |  |  |  |  |  |

## TABLE – 8

| Pressure and Flow requirements for high hazard installations with 20mm (K=115) sprinklers pre-calculated and pipe sizes from Tables 24 |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Minimum Design Density (lpm/m2) | Flow rate past installation valve (lpm) | Running pressure at the design point at the level of the highest sprinkler in the high hazard area (bars) |  |  |  |  |  |  |
|  |  | Floor area per sprinkler in m2 |  |  |  |  |  |  |
|  |  | 6 | 7 | 8 | 9 | 10 | 11* | 12* |
| 10.0 | 2800 |  |  |  | 1.0 | 1.2 | 1.4 | 1.7 |
| 12.5 | 4550 |  | 0.9 | 1.2 | 1.5 | 1.8 | 2.2 | 2.6 |
| 15.0 | 4550 | 1.0 | 1.3 | 1.7 | 2.1 | 2.6 | 3.1 | 3.7 |
| 17.5 | 4550 | 1.3 | 1.7 | 2.3 | 2.8 | 3.5 | 4.2 | 5.0 |
| 20.0 | 5600 | 1.7 | 2.3 | 3.0 | 3.7 | 4.6 | 5.6 | 6.6 |
| 22.5 | 5600 | 2.0 | 2.9 | 3.7 | 4.7 | 5.8 | 7.0 |  |
| 25.0 | 6750 | 2.6 | 3.5 | 4.6 | 5.8 | 7.1 |  |  |
| 27.5 | 6750 | 3.0 | 4.2 | 5.5 | 6.9 |  |  |  |
| 30.0 | 9000 | 3.6 | 5.0 | 6.5 |  |  |  |  |

*When an Ordinary hazard installation requires to be upgraded to high hazard, these parameters shall be used.

- The water supply running pressure at the installation valve "C" gauge shall not be less than either:

- Where the AMAO is not larger than the area protected i.e.

Pr + Pf + Ps      or

- Where the AMAO is larger than the area protected i.e.

Pred + Pf + Ps

Pred = running pressure as specified in tables 5, 6, 7 and 8 as appropriate at a flow rate equal to a value as indicated below:

Pred  = (Area protected/AMAO) X specified flow rate (in bar),

Pr = is the running pressure at the design point and flow rate specified in appropriate tables 5,6, 7, and 8  (in bar).

Pf  = is the calculated pipe friction loss between the installation valve "C" gauge and the most hydraulically remote design point, (in bar).

Ps = is the static pressure difference between the highest sprinkler downstream of the design point and the installation valve ‘C’ gauge, (in bar).

- WHERE AMAO IS FED BY MORE THAN ONE DISTRIBUTION PIPE: The pipe friction loss shall be calculated on the basis that the flow rates in the distribution pipes are in proportion to the fraction of the design area fed by each distribution pipe as shown in Figure 13.

- MIXED ORDINARY AND HIGH HAZARD: Where the area of the high-hazard protection is less than the AMAO but there is an adjacent area of ordinary hazard in the same room (i.e., an area in which sprinklers are liable to operate simultaneously), the high-hazard area flow rate required shall be reduced by the ratio of the actual area to the AMAO and to this flow rate shall be added the flow rate for the ordinary hazard area taken as 5.0 x the excess of the specified high-hazard AMAO over the actual high-hazard area (L/min). (see figure 14)

- When tested as described in appendix-- the water supply running pressure shall be based on the level of the highest sprinkler in the high-hazard area and shall be not less than that specified in rule 8.2.3.2.(see also rule 8.3 below)

- The ordinary-hazard portion of the installation shall be supplied as specified in 8.2.2, and the high-hazard distribution pipe feeding both high and ordinary-hazard sprinklers shall be of bore not less than as specified in the ordinary-hazard pipe tables.

- FULLY HYDRAULICALLY CALCULATED PIPE SIZE INSTALLATIONS:

- PRESSURE FLOW REQUIREMENTS: When tested as described in rule 18.3, the water supply running pressure at the 'C' gauge shall be not less than the value calculated by the method as narrated in rule 12.5. (4-sprinkler method)

- VELOCITY; The equilibrium water velocity shall not exceed 6 m/sec at any valve or flow monitoring device, or 10 m/sec at any other point in the system for the stabilized flow condition at the demand point involving an AMAO or, where the system includes intermediate sprinklers, the total number of sprinklers assumed to be in simultaneous operation.

+ + + +  + + + + + +  +

- PUMPS

- GENERAL REQUIREMENTS

- Pumps shall be exclusively used for the fire fighting purposes, be of a type approved by the committee, and shall be:-

- Electric motor driven centrifugal pumps.

or

- Compression ignition engine driven centrifugal pumps.

or

- Vertical turbine submersible pumps

In all the above cases, pumps shall be automatic in action.

- Pumps shall be direct-coupled, except in the case of engine-driven vertical turbine pumps wherein gear drives shall be used.  Belt-driven pumps shall not be accepted.

- Parts of pumps like impeller, shaft sleeve, wearing ring etc., shall be of non-corrosive metal preferably of brass or bronze.

Where seawater is used or where the quality of the water necessitates the use of special metals and alloys, the use of such metals and alloys shall be insisted upon.

- The capacity of the pump(s) would depend on the type of hazard protected and the same shall as per the sizes shown in the Table 9.

TABLE 9

PUMP SELECTION

| NATURE OF RISK | PUMP CAPACITY LPS (m3/hr.) | DELIVERY PRESSURE (Kg/m2) |
| --- | --- | --- |
| Light | 27 (96) | 5.6 |
|  | 30 (110) | 5.6 |
| Ordinary | 38 (127) | 5.6/7.0 |
|  | 47 (171) | 7.0 |
|  | 76 (273) | 7.0 |
| High | 47 (171) | 7.0 |
|  | 76 (273) | 7.0/8.8 |
|  | 114 (410) | 7.0/8.8 |

- Pumps shall be capable of furnishing not less than 150% of rated capacity at a head of not less than 65% of the rated head. The shut-off head shall not exceed 120% of rated head in case of horizontal pumps and 140% in case of vertical pumps.

- In case of electrically driven pumps, it is recommended that a compression ignition engine driven stationery of similar capacity be installed as a standby and vice versa.  However, where the sprinkler system consists of more than one pump, prime movers of all shall not be of same type.

Notwithstanding the above, if power to motorized fire pumps is obtained from two sources, one of which is a captive generating plant located in a block either 6M away from all surrounding building or, where this is not feasible, segregated from adjoining buildings in a manner indicated in rule 9.1.13, more than one pump may be of the electrically- driven type.

- In case of Jockey pumps in such systems to take care of minor leakages, the capacity thereof shall not be less than  3% and normally not more than 10% of the installed pumping capacity.

- Each pump shall be provided with a pressure gauge on the delivery side between the pump and the non-return valve and a plate giving the delivery head, capacity and the number of revolutions per minute.

- Each pump shall be provided with an independent suction pipe without any sluice or cut-off valves therein, unless the pump is situated below the level of the water supply in which case sluice or cut off valves would be essential, where the Net Positive Suction head (NPSH) available at site is less than 0.5 m in excess of the actual value, require at 150% of the duty point as per the manufacturers curves or where the water supply has fibrous or equally objectionable matter in suspension or mud and/or sand liable cause accumulation in the installation, suction pipe(s) shall be installed in a jack well fed through a culvert from the main water supply.  At the supply end of the culvert, a sluice or gate valve shall be provided.

- The diameter of the suction pipe shall be such that the rate of flow of water through it does not exceed 90 m per minute when the pump is delivering at its rated discharge, If, however, the pump is situated below the level of water supply, the diameter of the suction pipe/header shall be based upon a rate of flow of 120m per minute.

- Centrifugal pumps shall be fixed below the level of water supply. However, if the priming arrangements are such as to ensure that the suction pipe shall be automatically maintained full of water notwithstanding a serious leakage therefrom (the pump being automatically brought into action to replenish the priming tank should the later be drawn upon at a greater rate than the rate at which it is fed from any other source) , positive suction may not be insisted. In such cases, the capacity of priming tank need not exceed 450 litres and the diameter of the priming pipe need not exceed 50 mm.

NOTE:  For the purpose of rules 9.1.9, 9.1.10 and 9.1.11, a pump shall be considered as having positive suction only if the quantity of water in the reservoir above the level of the top of the pump casing is equivalent to the requirements in rule 7.1 of these regulations.

- If at the discretion of the committee, the pump is allowed to be installed above the level of its water supply, there shall be a foot valve and a priming arrangement, the latter consisting of a tank (having a capacity at least three times that of the suction pipe from the pump to the foot valve) connected to the delivery side of the pump by a metal pipe having a minimum internal diameter of 100 mm in the case of centrifugal pumps with a stop valve and a non-return valve therein of the same size. A dependable independent filling arrangement and a level indicator shall be provided for the priming tank. The provision of a vacuum gauge for the suction pipe is recommended.

- Pumps shall not be installed in the open. The pump room shall be so located as to be both easily accessible and where any falling masonry and the like from other buildings occasioned by fire other cause, cannot damage the pump room,. Normally, pump rooms shall be located 6m away from all surrounding buildings and overhead structures. Where this is not feasible, they may be attached to a building provided a perfect party wall complying with the committees regulations is constructed between the pump room and the attached building, the roof of the pump room is of R.C.C construction at least 100 mm thick and access to the pump room is from the outside. The pump rooms shall normally have brick/concrete walls and non-combustible roof, with adequate lighting, ventilation and drainage arrangements.

NOTE: The pump room shall be located 30 m clear of the equipment/vessels handling or storing flammable liquids/solvents and/or gases.

- ELECTRICALLY DRIVEN PUMPS:

- The sub-station(s) and/or DG House(s) supplying power to the fire pump(s) shall be of incombustible construction and shall be located at least 6m away from all surrounding buildings.  Where this is not feasible, all door and window openings of the surrounding buildings within 6M of the substation(s) and/or DG house(s) shall be protected by single fire doors and 6mm thick wired glass in steel framework respectively. Likewise, roof eaves, if any of the surrounding buildings falling within 6M of the substation(s) and/or DG house(s) shall be cut and wall raised as a parapet. The above provision shall also apply when the substation(s) and/or DG House (s) are within 6M of each other.

Where the substation(s) and/or DG House (s) are attached to buildings, perfect party walls complying with Committees rules shall be constructed to segregate the substation(s) and/or DG House (s) from the attached buildings and where the attached building is storied, the roof of the substation(s) and/or DG Houses shall be of RCC construction of at least 100mm thickness.

Transformer cubicles inside these sub-stations shall be separated from HT/LT cubicles and from each other by blank brick/stone/concrete walls of 355 mm thickness or of RCC of 200mm with door openings, if any, therein being protected by single fireproof doors complying with the Committee's regulations.  The  sub-station(s) and DG Houses shall also be separated from each other as above.

Transformers installed outdoors which are supplying power to fire pump(s), shall also be located at least 6M away from all the surrounding buildings [(including substation(s) and/or DG House (s)]. Where this is not feasible, all door and window openings of the surrounding buildings [(including substation(s) and/or DG House (s)] within 6M of the of the transformers shall be protected by single fire doors and 6mm thick wired glass in steel framework respectively.  Likewise, roof eaves, if any of the surrounding buildings falling within 6M of the transformers shall be cut and wall raised as a parapet.  Blast walls of bricks/stone/concrete blocks of 355mm thickness or of RCC of 200mm thickness shall be constructed between two transformers and these walls shall be extended horizontally by 600mm beyond the extremities of the transformers and vertically 600mm above the highest point of the transformers.

NOTE:  For High Hazard (B) occupancies, substation(s) supplying power to fire pumps shall, in addition to complying with the above provisions, be located 30M clear of all equipment where flammable fluids having a flash point below 65°C are handled and/or stored.

- Overhead feeders to sub-station(s) supplying power to the fire pump(s) are not permitted within a horizontal distance of :

- 15m of any process building/plant or tanks containing flammable liquids or

- 6m of any other building or tanks containing non-flammable liquids or of storage in open.

In case the feed to such sub-station(s) is by means of under ground cables, the cables shall not pass under any building or permanent structure.

- Sufficient spare power shall always be available to drive pumping set(s) at all times throughout the year.

- The electric supply to the pumping set(s) shall be entirely independent of all other equipment in the premises i.e., even when the power throughout the entire premises is switched off, the supply to the pump shall continue to be available interrupted. This can be achieved by taking the connection for the pump(s) from the incoming side of the main LT breaker. However, in cases where two or more transformers and/or sources of supply are connected to a common bus bar or where there is provision of a bus coupler between the busbar sections, the connection may be taken through the bus bars. (Figure 15).

- The fire pump circuit shall be protected at the origin by an automatic circuit breaker so set as to permit the motor to be overloaded during an emergency to the maximum limit permissible by the manufacturers. Further, the under- voltage release/no volt coil of the circuit breaker shall be removed.

NOTE: Where cable lengths are long enough to warrant back- up protection, the Committee may insist on provision for such a protection.

- It is recommended that telltale lamps which could continuously glow when power is available to the fire pump(s) circuit be provided and fixed in a prominent position, both in the sub-station and in the pump room.

- A direct feeder without any tappings, shall be laid from the sub-station to the pump house. The feeder shall be laid underground and shall not pass under any building or permanent structure. Under extraneous circumstances, the Committee may permit use of overhead cables, but in no case shall such cables be permitted to contravene the distance indicated in rule 9.2.2.

- Where there is more than one source of power for the operation of pumping set(s) every electrical circuit shall preferably be so designed as to ensure that when necessary the set(s) continue to operate without the manual operation of an emergency switch.

- The pumping set(s) shall be securely mounted on a robust bedplate, if of the horizontal type, and shall be free from vibration at all variations of load.

- The rating and design of motors and switchgear shall conform to the relevant Indian Standards Specifications. The Motor shall be of continuous rating type and its ratings shall be equivalent to the horse power required to drive the pump at 150% of its rated discharge.  (see rule 9.1.4)

- The motor shall be of totally enclosed type or drip proof type, the latter having their air inlets and outlets protected with meshed wire panels to exclude rodents, reptiles and insects.

- The motor(s) shall be wound for class B insulation preferably for class E - and the windings shall be vacuum impregnated with heat and moisture resisting varnish and preferably glass fibre insulated to withstand tropical conditions.

- Motor(s) wound for high tension supplies shall have a suitable fixed warming resistance to maintain the motor windings in a dry condition at all times and particularly under monsoon conditions. The resistance shall be connected to the lighting or other equivalent circuit.

- Heating apparatus shall also be provided, when necessary, for medium tension motor where they are located below ground level, in order to maintain the motor windings in a dry condition. Adequate drainage arrangements shall also be provided in the pump house in such cases.

- The incoming cable to the fire pump room shall terminate in an isolating switch fuse unit incorporating the HRC fuses and where necessary provided with a distribution system.

- The starting switch gear for the fire pumps shall be suitable for direct on line starting but other alternative arrangements are subject to prior approval. It shall also incorporate an ammeter with a clear indication of the motor full load current.

NOTE: Remote controlled starting arrangements are subject to prior approval of the committee.

- Cables for motors and switchgears shall be armoured or enclosed in heavy gauge screwed steel conduit according to conditions.

- It is recommended that the equipment throughout be painted fire red (shade no 536 as per IS:5) and suitably marked for identification

- Necessary spare parts including a set of fuses ( in a glass fronted box) shall be kept in readiness at all times in the pump house.

- The wiring in all installations shall be done in accordance with the regulations for the electrical equipment of building issued by the Tariff Advisory Committee.

- COMPRESSION IGNITION ENGINE DRIVEN PUMPS

- PUMP ROOM: The pump room shall be artificially heated, if necessary, to maintain the temperature of the room above 10°C.  Adequate ventilation shall be provided for the air required for aspiration and to limit the temperature rise in the room to 10°C above the ambient temperature when the engine is on full load.

- ENGINE:

- The engine shall be:

- Of the compression ignition mechanical direct injection type, capable of being started without the use of wicks, cartridges, heater plugs or ether, at an engine room temperature of 7°C and shall accept full load within 15 seconds from the receipt of the signal to start.

- Naturally aspirated, supercharged or turbocharged and either air or water cooled. In the case of charged air cooling by means of a belt driven fan or of a belt driven auxiliary water pump there shall be multiple belts such that should half the belts break, the remaining belts would be capable of driving the fan or pump.

- Capable of operating continuously on full load at the site elevation for a period of six hours.

- Provided with an adjustable governor to control the engine speed within 10% of its rated speed under any conditions of load up to the full load rating. The governor shall be set to maintain the rated pump speed at maximum pump load.

- provided with an in-built tachometer to indicate the RPM of the engine.

- provided with a time totaliser (Hour counter)

- Any manual device fitted to the engine which could prevent the engine starting shall return automatically to the normal position.

- Engines, after correction for altitude and ambient temp.  shall have bare engine horsepower rating equivalent to the higher of the following two valves.

- 20% in excess of the maximum brake horsepower required to drive the pump at its duty point.

- The brake horsepower required to drive the pump at 150% of its rated discharge.

- The coupling between the engine and the pump shall allow each unit to be removed without disturbing the other.

- COOLING SYSTEM:

The following systems are acceptable

- Cooling by water from the discharge of fire pump (taken off prior to the pump discharge valve) direct into the engine cylinder jackets via a pressure reducing device to limit the applied pressure to a safe value as specified by the engine manufacturer.  The outlet connection from this system shall terminate at least 150 mm above the engine water outlet pipe and be directed into an open tundish so that the discharge water is visible.

- a heat exchanger, the raw water being supplied from the fire pump discharge (taken off prior to the pump discharge valve) via a pressure reducing device, if necessary, to limit the applied pressure to a safe value as specified by the engine manufacturer. The raw water outlet connection shall be so designed that the discharged water can be readily observed. The water in the closed circuits shall not be less than that recommended by the engine manufacturer. If the auxiliary pump is belt driven there shall be multiple belts so that should half the belts break, the remaining belts shall be capable of driving the pump.

- a frame or engine mounted air cooled radiator with a multiple belts driven fan from the engine. When half the belts are broken the remaining belts shall be capable of driving the fan. The water in the closed circuit shall be circulated by means of the auxiliary pump driven by the engine and the capacity of the closed circuit shall be not less than that recommended by the engine manufacturer.

- direct air cooling of the engine by means of multiple belts driven fan. When half the belts are broken the remaining belts shall be capable of driving the fan.

NOTE:    In case of systems described in b, c, and d, above a failure actuated audio-visual alarm shall be incorporated.

- AIR FILTRATION: The air intake shall be fitted with the filter of adequate size to prevent foreign matter entering the engine.

- EXHAUST SYSTEM:  The exhaust shall be fitted with a suitable silencer and the total backpressure shall not exceed the engine maker's recommendation. When the exhaust system rises above the engine, means shall be provided to prevent any condensate flowing into the engine.

- Engine shutdown mechanism: This shall be manually operated and return automatically to the starting position after use.

- FUEL SYSTEM

- FUEL: The engine fuel oil shall be of quality and grade specified by engine makers. There shall be kept on hand at all times sufficient fuel to run the engine on full load for three hours, in addition to that in the fuel tank.

- FUEL TANK: The fuel tank shall be of welded steel construction relevant to Indian or foreign standard for mild steel drums.  The tank shall be mounted above the engine fuel pump; to provide a gravity feed unless otherwise recommended by the manufacturers. The tank shall be fitted with an indicator showing the level of fuel in the tank. The capacity of the tank shall be sufficient to allow the engine to run on full load for

Light hazard           	1 hour;

Ordinary hazard	2 hours;

High hazard 		3 hours.

NOTE:    Where is more than one compression ignition engine driven pump set there shall be separate fuel tank and fuel feed pipe for each engine.

- Fuel Feed pipes: Any valve in the fuel feed pipe between the fuel tank and the engine shall be placed adjacent to the tank and it shall be locked in the open position. Pipe joints shall not be soldered and plastic tubing shall not be used.

- AUXILIARY EQUIPMENT: The following shall be provided:

- a sludge and sediment trap, b) a fuel level gauge,  c) an inspection and cleaning hole,  d) a filter between the fuel tank and fuel pump mounted in an accessible position for cleaning, e) means to enable the entire fuel system to be bled of air. Air relief cocks are not allowed; Screwed Plugs are permitted.

- STARTING MECHANISM: Provision shall be made for two separate methods of engine starting, viz.,

- Automatic starting by means of a battery powered electric starter motor incorporating the axial displacement type of pinion, having automatic repeat start facilities initiated by a fall in pressure in the water supply pipe to the spray installation. The battery capacity shall be adequate for ten consecutive starts without recharging with a cold engine under full compression.

- Manual starting by:

  - Crank handle, if engine size permits

or

  - Electric starter motor.

NOTE:    The starter motor used for automatic starting may also be used for manual starting provided there are separate batteries for manual starting.

- BATTERY CHARGING: The means of charging the batteries shall be by a 2-rate trickle charger with manual selection of boost charge and the batteries shall be charged in position. Where separate batteries are provided for automatic and manual starting the charging equipment shall be capable of trickle charging both the batteries simultaneously.  Equipment shall be provided to enable the state of charge of the batteries to be determined.

- TOOLS: A standard kit of tools shall be provided with the engine and kept on hand at all times.

- Spare parts: The following spare parts shall be supplied with the engine and kept on hand.

- Two sets of fuel filters, elements and seals,

- two sets of lubricating oil filters, elements and seals.

- two sets of belts (wherever used)

- one complete set of engine joints, gaskets and hoses.

- two injector nozzles

- one complete set of piston rings for each cylinder

- one inlet valve and one exhaust valve.

- ENGINE EXERCISING:

The test shall be for a period of at least five minutes each day. Where closed circuits cooling systems are used the water level in the primary system shall be checked at the time of carrying out each test and, if necessary, water shall be added during the course of test procedure.

- A written declaration shall be given that the following conditions will strictly complied with:

- to test the engine at least once a week

- to maintain the temperature of the engine room at not less than 4.5 degree C at all times,

- to maintain the minimum, quantity of fuel oil required as desired in these clauses

- to use a good grade of fuel oil equivalent in quality to that specified by the engine maker

- to keep on hand the spare parts required as specified above.

+ + + + + + + + + +

- PIPING AND SUPPORTS.

- PIPING.

- The pipe used in the sprinkler system (from the pump house to the installation valves) shall be laid normally laid underground or in masonry culverts with removable covers of incombustible construction and shall be of any one of the following types: -

- Cast iron double flanged class "A" pipes conforming to the following standards:

| - Horizontally Cast iron pipes | IS-7181 |
| --- | --- |
| - Vertically Cast iron pipes | IS-1537 |
| - Centrifugally Cast (spun) iron pipes | IS-1536 |

NOTE:   In case of vertically Cast iron pipes, where the nominal diameter of the pipes exceeds 300 mm or where the pump delivery pressure exceeds 7 Kg/cm², class "B" pipes would be necessary.

- Centrifugally Cast (spun) iron class "A" pipes with Tyton joints conforming to IS-1536.

- Wrought or mild steel pipes (galvanised or not) of heavy grade conforming to IS-1239 and IS-1978 (when installed underground) or Electric resistance welded steel pipes conforming to IS-3589 having welded joints and coated and wrapped as per IS-10221-Code of practice for coating and wrapping of underground mild steel pipelines.

- Welded and Seamless pipe as per ASTM-A53.

- Electric resistance welded steel pipes conforming to ASTM-A135.

- Wrought steel pipe conforming to ASTM-B36.10

NOTE: - At least 10% of all the welded joints shall be radiographically tested and half of the joints radiographed shall be field joints.

- Pipes may be laid overground on exclusive supports. Pipes shall be of material conforming to any of the descriptions as per rule 10.1.1 c, d, e or f with welded, threaded or flanged joints and supported adequately as per piping manual at regular intervals. The pipes shall run at least at distances from the face of the building(s) and/or open storage area(s) as stipulated below -

| Light hazard | 6M | Ordinary hazard | 6M | High hazard | 15M |
| --- | --- | --- | --- | --- | --- |

- Underground pipes shall be laid not less than 1M below ground level. Where soil conditions are unsatisfactory, masonry or equivalent supports shall be provided at regular intervals.

NOTE:   In case of poor soil conditions, it may sometimes be necessary to provide continuous masonry or equivalent supports.

- Pipes shall not be laid under buildings or plant areas or storage areas. As far as possible, pipes shall not be laid under large open storage, railroads and roads carrying heavy traffic.

- Pipes shall not traverse on ground, which is not under the control of the owner of the installation. Pipes shall also not pass through public roadways.

- The installation piping (from the pump house up to the installation valve and also the installation piping with sprinklers) shall be capable of withstanding for two hours a pressure equivalent to 150% of the maximum working pressure.

- All boltholes in the flanges shall be drilled. Drilling of each flange shall be in accordance with the relevant Indian or ASTM or British standards.

- Flanges shall be faced and have jointing of rubber insertions or asbestos compound.

- Welded joints shall not be permitted for pipes having diameter less than 50 mm.

NOTE:   Where joints with odd angles are encountered, reference shall be made to the Committee in advance.

- It is not permissible to run the sprinkler pipes through an un-sprinklered building or occupancy and where it is not practicable the supply pipeline shall be installed at ground level and enclosed in brick trenches covered with removable RCC pre-cast slabs.

- All installation pipework above ground shall be installed at a slope not less than 1: 500 for horizontal run of pipes.  Normally the pipework should slope through the installation valve. If the pipework is trapped (below the level of the installation valve for example in the basements), arrangements shall be made to provide drain cocks at the bottom of such pipes to drain the trapped water.

- Sprinkler pipes shall not be embedded in concrete floors or ceilings of any building.

- FITTINGS.

- Fittings installed underground shall be of Cast iron heavy grade conforming to IS-1538 or BS-2035/4346 whereas those installed overground shall be of medium grade wrought or mild steel conforming to IS-1239 (part II) or malleable iron fittings conforming to IS-1879 (part I to X).

- All fittings shall be able to withstand at least a pressure of 150% of the maximum working pressure.

- Welded fittings according to the laid down welding procedure are permitted. Welded parts shall be galvanised or suitably coated after welding as per the requirement of the areas to be protected by the system i.e. chemical and electrolytic corrosion.

- Welded joints shall not be permitted for fittings of less than 50 mm diameter.

- SUPPORTS (PIPES AND FITTINGS ABOVE INSTALLATION VALVE).

- Sprinkler pipes shall be supported from the building structure which itself shall be capable of supporting the water filled pipework and shall not impair the performance of sprinklers under fire conditions.

- Pipework shall not be used to support any other loads except where primary support is designed for the suspension of the piped service.

- Distribution/Range pipes shall not be supported from ceiling sheathing or cladding or from any other associated suspension systems.

- Pipes below obstructions such as ductwork shall be either supported from the building structure or from the steel members supporting such obstructions. Such members shall be capable of supporting the weight of water filled pipes too.

- Hangers shall not be welded or fastened directly to the pipework.

- The supports on which the pipework rests shall be secured firmly in position.

- The thickness of all parts of pipe supports shall not be less than 3 mm.

- Wherever possible, pipes shall be supported from non-combustible building elements.

- Pipework in corrosive areas shall be of either stainless steel or suitably protected against corrosion.

- The distance between the pipe supports measured along the line of connected pipes (whether the pipes run horizontally, vertically or at angles) shall not be less than the following Table 10.

TABLE – 10

| PIPE DIAMETER | SPACING |
| --- | --- |
| Up to 65 mm | 4.0M |
| 65 mm to 100 mm | 6.0M |
| 100 mm to 250 mm | 6.5M |

- DISTRIBUTION PIPES

- The first support on a nominally horizontal distribution pipe shall not be at more than 2 M from the main distribution pipe.

- The last support on a nominally horizontal distribution pipe shall not be more than 450 mm from the end.

- Drop or rise pipes shall be secured to the building structure either directly or indirectly at the adjacent nominally horizontal part of the pipe within 300 mm of the drop or rise.

- RANGE PIPES

- At least one support shall be provided for

  - Each pipe run connecting adjacent sprinkler, and

  - The pipe run connecting the distribution pipe and the first sprinkler on the range pipe.

- Pipe supports shall not be closer than 150 mm to any sprinkler axial central line.

- The first support on a range pipe shall not be more than 2 M from the distribution pipe

- The last support on a range pipe shall not be at more than 1.5 M from

  - The range pipe end or

  - Where there is a horizontal arm pipe of 450 mm or longer, the arm pipe end: or

  - Where there is a drop or rise exceeding 600 mm, the drop or rise pipe end.

  - Outgoing mains from the Installation valve to the system shall be supported at every 3.5 M of its run.

- The thickness of all components used in pipe supports shall not be less than 3 mm anywhere.

- Some of the typical supporting arrangements are shown in Figure 15(a).

- SPRINKLER SPACING, ARRANGEMENT AND LOCATION.

- GENERAL REQUIREMENTS.

- All the measurements between sprinklers or of areas covered by groups of individual sprinklers shall be taken in the horizontal plane.

Notwithstanding the above provisions, the hydraulic calculations shall show the dimensions of the true lengths measured along the slope of the pipe.

- Sprinklers shall be installed upright or pendent as required under the circumstances, with the deflector parallel to the slope of the roof, ceiling or pitch line of stairs.

- Where the slope of the roof is greater than 1 in 3, a line of sprinklers shall be fitted at the apex unless there is a row of sprinklers at not more than 750 mm distant radially therefrom.

- COVERAGE AND SPACING OF SPRINKLERS

- LIGHT HAZARD CLASS

- Maximum area coverage per sprinkler:

| - Sidewall sprinklers | 17 m² |
| --- | --- |
| - Other types of sprinklers | 21m² |

- Maximum distance between sprinklers on range pipes and between adjacent rows of sprinklers:

| - Sidewall sprinklers | 4.5 m* |
| --- | --- |
| - Other types of sprinklers | 4.5m |

*For rooms exceeding 3.7M but within 7.4 m in width, one row of sprinklers shall be provided on each wall at the above spacing and if the length of the room exceeds 9.2 m, the sprinklers in the opposite walls shall be staggered.[Figure 16(a)]

- Minimum spacing between sprinklers:

Sprinklers shall not be spaced at less than 2M except in locations where the heat sensitive elements of the sprinklers can be protected from wetting of the operation of the adjoining sprinkler by suitable baffles with the prior approval of the Committee. (Figure 17)

- DISTANCE BETWEEN SPRINKLERS AND THE BOUNDARY: (Figure 17)

- The distance between the boundary and sprinklers when measured along the range pipe shall not be more than 0.5 times the spacing between the sprinklers and when measured perpendicular to the range pipe shall not be more than 0.5 times the spacing between the range pipes.

- However, where the external walls are combustible or built with asbestos and Metal or open sided and also in case of open joisted ceilings or where the roof has the rafters exposed, the distance between the boundary and the sprinklers shall not exceed 1.5M.

- Sidewall sprinklers shall be located with the deflector vertical centre line not less than 50 mm and not more than 150 mm from the wall face against which they are mounted.

- ORDINARY HAZARD CLASS

- MAXIMUM AREA COVERAGE PER SPRINKLER:

| - Sidewall sprinklers | 9 m2 |
| --- | --- |
| - Other types of sprinklers | 12 m2 |

- MAXIMUM DISTANCE BETWEEN SPRINKLERS ON RANGE PIPES AND BETWEEN ADJACENT ROWS OF SPRINKLERS:

| - Sidewall sprinklers | 3.4 m* |
| --- | --- |
| - Other types of sprinklers -- |  |
| - With standard spacing | 4.0 m |
| - With staggered spacing sprinklers on ranges | 4.6 m |
| - Adjacent rows | 4.0 m |

*For rooms exceeding 3.7M but within 7.4M in width, one row of sprinklers shall be provided on each wall at the above spacing and the sprinklers in the opposite walls shall be staggered as shown in the Figure 16(a). If the width of the room exceeds 7.4M, it is necessary to sprinkler the central portion by conventional ceiling sprinklers and the distance between the above and the sidewall sprinklers shall not be less than 3.7M. [Figure 16(b)]

- MINIMUM SPACING BETWEEN SPRINKLERS:

Sprinklers shall not be spaced at less than 2M except in locations where the heat sensitive elements of the sprinklers can be protected from wetting of the operation of the adjoining sprinkler by suitable baffles with the prior approval of the Committee. (Figure 17)

- DISTANCE BETWEEN SPRINKLERS AND THE BOUNDARY: (Figure 17)

- The distance between the boundary and sprinklers when measured along the range pipe shall not be more than 0.5 times the spacing between the sprinklers and when measured perpendicular to the range pipe shall not be more than 0.5 times the spacing between the range pipes.

- However when the lay out is staggered, the distance between the boundary and the sprinklers when measured on range perpendicular to the boundary shall not be more than 0.5 times and 0.25 times the spacing between the sprinklers on alternate range lines.

- However, where the external walls are combustible or built with asbestos and Metal or open sided and also in case of open joisted ceilings or where the roof has the rafters exposed, the distance between the boundary and the sprinklers shall not exceed 1.5M.

- Side wall sprinklers shall be located with the deflector vertical centre line not less than 50 mm and not more than 150 mm from the wall face against they are mounted.

- HIGH HAZARD CLASS

- MAXIMUM AREA COVERAGE PER SPRINKLER:

| - In general | 9 m² |
| --- | --- |
| - In storage racks (intermediate) |  |
| - With a single row of sprinklers | 10 m² |
| - With a double row of sprinklers | 7.5 m² |

- MAXIMUM DISTANCE BETWEEN SPRINKLERS ON RANGE PIPES AND BETWEEN ADJACENT ROWS OF SPRINKLERS:

| - In general | 3.7 m* |
| --- | --- |
| - Within storage racks (intermediate) | 2.5 m |

- MINIMUM SPACING BETWEEN SPRINKLERS:

Sprinklers shall not be spaced at less than 2M except in locations where the heat sensitive elements of the sprinklers can be protected from wetting of the operation of the adjoining sprinkler by suitable baffles with the prior approval of the Committee. (Figure 17)

- DISTANCE BETWEEN SPRINKLERS AND THE BOUNDARY: (Figure 17)

- The distance between the boundary and sprinklers when measured along the range pipe shall not be more than 0.5 times the spacing between the sprinklers and when measured perpendicular to the range pipe shall not be more than 0.5 times the spacing between the range pipes.

- However, where the external walls are combustible or built with asbestos and Metal or open sided and also in case of open joisted ceilings or where the roof has the rafters exposed, the distance between the boundary and the sprinklers shall not exceed 1.5M.

- Sidewall sprinklers and staggered layout for the installation are not permitted in high hazard risks.

- SPACING BELOW SPRINKLER HEADS:

A clear space of 0.5M shall be maintained below the deflector of the sprinkler heads in all cases except high piled combustible storage areas/Jute storage and above open suspended ceilings where the clear space required as above shall be 1M.

- LOCATION OF SPRINKLERS IN RELATION TO BUILDING STRUCTURE AND PLANT:

- ROOFS AND CEILINGS

- ROOFS AND CEILINGS, WITHOUT BEAMS OR BAYS: -

- For conventional and spray type of sprinklers, the sprinklers shall be installed in such a way that the deflectors are at distances as shown in Table 11.

- For sidewall sprinklers, the deflector of the sprinklers shall be not less than 100 mm and not more than 150 mm below the ceiling.

TABLE - 11

| Type of ceiling | # Distance in Millemetres |  |  |
| --- | --- | --- | --- |
|  | Minimum | Maximum | Preferred |
| - Combustible, Asbestos Cement sheets, Wired glass and other types of frangible elements | 75 | 300 | 150 |
| - Combustible with exposed rafters and/ or open joists | 75 | 150 | --- |
| - Non combustible -- either plane or arched or sloping | 75 | 150 | 150 |

TABLE - 12

SPRINKLER LOCATION IN RELATION TO BEAMS AND JOISTS

| Minimum horizontal distance from sprinkler vertical axis to the side of beam or joist (in mm) (a) (Also see Figure 18) | Maximum height of sprinkler deflector above (+) or below (-) bottom of beam (b) or joist (in mm) (Also see Figure 18) |  |  |  |
| --- | --- | --- | --- | --- |
|  | Conventional sprinkler |  | Spray sprinkler |  |
|  | Installed upright | Installed pendent | Installed upright | Installed pendent |
| 200 | - 20 |  |  |  |
| 400 | 0 |  | 0 | 0 |
| 600 | + 30 |  | + 20 | + 60 |
| 800 | + 60 |  | + 30 | + 120 |
| 1000 | +100 | - 200 | + 50 | + 200 |
| 1200 | +140 | -170 | +100 | + 280 |
| 1400 | +190 | -120 | +130 | + 360 |
| 1600 | +260 | - 30 | +160 | + 470 |
| 1800 | +390 | +170 | +180 | + 670 |

*These types are not used at these horizontal distances

- Roofs and ceilings, with beams but without bays:-

- In case of conventional and spray type of sprinklers where a beam or joist is so deep that a sprinkler can not be located below the beam or joist as specified in the table under rule 11.4.1.1 above, they shall be located above the base of the beam or joist at a distance below the ceiling and at a distance horizontal from the beam/joist as specified in Table 12  (depth of beam/joist less than 300/450mm) (Figure 18)

- In case of sidewall sprinklers any beam or other obstruction below the ceiling within the rectangle centered on the sprinkler, of dimension A X 2B shall not exceed the depth as in the table 13.

TABLE - 13

SIDEWALL SPRINKLER LOCATION IN RELATION TO BEAMS

| Depth of beam (mm) |  | Minimum horizontal distance between sprinkler/wall to beam (in M) |  |
| --- | --- | --- | --- |
| More than | Less than | Perpendicular to wall dimension “A” | Parallel to wall either side of sprinkler dimension ‘B’ |
| 0 | 100 | 1.8 | 1.0 |
| 100 | 125 | 2.1 | 1.2 |
| 125 | 150 | 2.4 | 1.4 |
| 150 | 175 | 2.7 | 1.6 |
| 175 | 200 | 3.0 | 1.8 |

NOTE:  Any obstruction below the plane of the ceiling within a rectangle either side of the sprinkler by 1.8M shall be regarded as a boundary.

- ROOFS AND CEILINGS, WITH BAYS AND/OR DEEP BEAMS: -

- Where the depth of a beam or joist exceeds 300 mm or 450 mm for combustible and non-combustible ceilings respectively or other similar obstructions form ceiling bays so that requirements under rule 11.4.1.1 cannot be met, then the beam or joist or any other such obstructions shall be regarded as a boundary.

- Where the distance between centre to centre of beams or joists is 1.8M or less, the above parameters do not hold good and reference shall be made to the Committee with full particulars.

- For roofs of construction other than the types specified in rules in this section and Table 11, the Committee shall be approached in advance with full particulars as these rules do not cater to protection for such types.

- COLUMNS

As far as possible, the sprinklers shall be located away from the columns. Where a roof or ceiling sprinkler is less than 0.6M from the face of a column, another sprinkler shall be located not more than 2M from the opposite side of the column

- GIRDERS

- Where the top flange of a girder is not more than 200 mm in width, sprinklers shall be either positioned either not less than 1.2M from the side of the girder or directly above the girder with the deflector not less than 150 mm from the top face of the girder.

- Where the top flange of the girder is more than 200 mm in width, sprinklers shall be positioned not less than 1.2M from the side of the girder.

- ROOF TRUSSES

- Where the roof truss members are not more than 100 mm wide, sprinkler shall be positioned either not less than 0.3M from the side of the truss or equidistant from each side of the truss with the deflector not less than 150 mm above any truss member.

- Where the truss members more than 100 mm but less than 200 mm wide, sprinkler shall be positioned either not less than 0.6M from the side of the truss or equidistant from each side of the truss with the deflector not less than 150 mm above any truss member.

- Where the truss members are more than 200 mm wide, sprinklers shall be positioned not less than 0.6M from the sides of the truss.

- CONCEALED SPACES

- ROOF SPACES: Spaces between roofs and ceilings (including those at the apexes and sides of buildings) more than 0.8M deep measured between the highest point under the roof and the top of the ceiling shall be sprinkler protected.

- INTERMEDIATE FLOOR SPACES: Concealed spaces between floors and ceilings shall be sprinklered where they are as follows:

- More than 0.8M deep; or

- Not wholly of non-combustible construction; or

- Containing combustible materials.

- SPACE UNDER LOWEST FLOOR: Sprinklers shall be installed in all spaces below the lowest floors in a building where the floor is combustible and:

- the space is accessible for storage purpose and/or entrance of unauthorized persons and/or accumulation of waste and debris and/or is not sealed against liquid spillage; and

- the space contains utility piping and installation such as air, steam, wiring, shafting, conveyors etc.,

- flammable liquids are stored in the floor above.

- BINS AND SILOS: Where the area of the Bins and Silos exceed 9M2 and where the same are detached, sprinklers shall be provided inside the Bins and Silos containing sawdust, wood flour, pulverized coal and similar ignitable materials. Care should be exercised to ensure that for materials, which tend to swell under water and burst, reference shall be made to the Committee in advance with full particulars.

- CORN, RICE, PROVENDER AND OIL MILLS:

- A sprinkler shall be fitted at the head of each dust trunk.  Sprinklers shall be installed at not more than 3M apart in all dust trunks which are constructed of combustible materials and which are installed at more than 30o from the vertical.

- Tiers of cyclones (centrifuges), or similar plant, separated by less than 1M shall be protected by sprinklers in the interspace as shown in the Figure 19.

- ELEVATORS, ROPE OR STRAP RACES, GEARING BOXES AND DUST RECEIVERS:

- Elevators, other than pneumatic elevators or slow moving endless chain, ring, loop or fork elevators capable of operating only when the elevator is full, shall be fitted with a sprinkler. The sprinkler shall be in the box at the top, located to discharge over the head and both legs or shafts of the elevator.

- Rope or strap races, gearing boxes and enclosed shaft machine drives of combustible construction or communicating between floors, shall be fitted with internal sprinklers.

- Dust cyclones and dust collection chambers and boxes either inside the protected building or outside and directly above any protected building with a combustible roof, shall be fitted with internal sprinklers.

- The trunkings connecting the dust collection chambers to the protected building within 10M shall be protected with sprinklers.

- ESCALATORS:  Sprinklers shall be installed in the following areas:

- In the passenger carrying space;

- Below the ceiling below the escalator;

- Between the ceiling below the escalator and the passenger carrying space;

- In the escalator boot;

- In the motor areas.

- HOISTS, LIFT WELLS AND ENCLOSED CHUTES THROUGH THE FLOORS:  The above areas, if not segregated from the main buildings in which they are located, shall be sprinklered.

- MACHINERY PITS AND PRODUCTION LINES:  Machinery pits in which combustible wastes may accumulate and the undersides of the production lines shall be sprinklered.

- ENCLOSED PAINT LINES, DRYING OVENS AND DRYING ENCLOSURES: The above areas shall be sprinklered on the inside and sidewall sprinklers may be considered for these areas.

- OBSTRUCTION BELOW SPRINKLERS

- Sprinklers shall be fitted under the following types of obstructions which are either a) more than 0.8M wide and less than 150mm from the adjacent walls or partitions or b) more than 1M wide.

Internal overhead platforms, Heating panels, Galleries, Walkways, Stagings other than in film or television studios and Stairs and stairways unless specifically excepted.

- DUCTS:   Sprinklers shall be fitted below the ducts under the following circumstances:

- rectangular and more than 0.8M wide and less than 150mm from the   adjacent  walls or partitions;

- circular and more than 1M in diameter and less than 150mm from the   adjacent walls or partitions;

- rectangular and more than 1M in width;

- circular and more than 1M in diameter.

- HOODS OVER PAPER MAKING MACHINES: Sprinklers shall be fitted under the hoods or shields over the dry ends of above machines. If there is an enclosures, side wall sprinklers are recommended.

- STORAGE RACKS: Sprinklers shall be fitted to protect the storage in racks.

- WORKTABLES: Sprinklers shall be fitted under the worktables where there is a power source or where combustible process waste may accumulate.

- SUSPENDED CEILINGS: For protecting the suspended imperforate or open ceilings with sprinklers, Committee shall be approached well in advance for suitable advice as the protection needs special considerations due to several factors like combustibility of the roof material, behaviour under fire conditions, structural integrity etc.,

- CANOPIES: Canopies that are non-combustible and less than 2M from the wall of the building need not be protected with sprinklers provided cut-off sprinklers are fitted at the door openings leading to the canopies. However, under other circumstances, the underside of the canopies shall be fitted with sprinklers.

- EXTERIOR DOCKS AND PLATFORMS: Sprinklers shall be fitted under the exterior docks and platforms of combustible construction unless such spaces are sealed against accumulation of debris and waste.

- SPRINKLER PROTECTION FOR SPECIFIC HAZARDS

- FILM AND TELEVISION PRODUCTION STUDIOS: Sprinklers shall be fitted under solid or slated platforms [except those used for temporary platforms etc. for sets but including those for lighting and other equipment] if these are more than 0.8M wide and also for walkways, connecting stairs including those used for lighting and other equipment. Sprinklers shall also be fitted in concealed spaces or cavities more than 100mm deep between combustible linings and walls/roofs.

- THEATRES AND SIMILAR PREMISES: In addition to the sprinklers in the roof or ceiling, sprinklers shall be fitted under the grid, the flies, the stage and any other obstruction to the discharge from the roof or ceiling sprinklers. Care shall be exercised in siting the sprinklers and associated pipework in case where moving sets are involved and also where personnel have to work in the close proximity of the sprinklers.

- COMPUTER AND SIMILAR EDP AREAS:  Pre-action sprinkler installation is recommended for above type of risks keeping in mind the effect of water discharge on such risks

- PLASTIC ROOF LIGHTS:  Sprinklers shall not be installed directly below roof lights of PVC or plastics of similar thermal behaviour and shall only be installed where a) the area of rooflight does not exceed 5M2,b) the distance between the individual rooflights is not less than 1.8M and c) the total area of rooflights in any building or in those communicating therewith does not exceed 15% of the plan area of such building(s).

- COLD STORAGE WAREHOUSE: As the nature of protection shall differ from risk to risk, Committee shall be approached with full details in advance for designing sprinkler protection for cold storage areas.

- INTERMEDIATE LEVEL SPRINKLERS: For high hazard storage in racks, shelves etc., protection by rows of intermediate sprinklers is mandatory, if storage heights are beyond the limits specified in rules 8.1.5.2 and 8.1.5.3 (Tables 3 and 4).  The requirements for the above provisions are as under:

- The location of sprinklers shall be such that they are not obstructed by racks or structural steel work and as far as possible, they are in the path of longitudinal flue space.  The discharge of water shall be able to penetrate the goods stored in the racks. The clearance between the sprinkler deflectors and the stored goods shall not be less than 150 mm anywhere.  The numbers of rows are determined by the height of the racks and/or shelves.

- The horizontal spacing (longitudinal) between sprinklers shall not exceed 3.5M for Category I/II goods and 1.8M for Category III/IV goods. Laterally for every 3M width of the racks (including two racks when stored back to back), there shall be one sprinkler.

- The vertical spacing between sprinklers shall not exceed 3M. If the top tier of the racks is within 3M of the roof sprinklers, top tier need not be protected with intermediate sprinklers.

- The location of intermediate sprinklers shall be such that the product of the horizontal and vertical spacing between sprinklers is not more than 9M2 for Category I/II storage goods and 5M2 for Category III/IV storage goods.

NOTE: Attention is also invited to rule 12.6 for the installation and piping requirements for intermediate sprinklers.

+ + + +  + + + + +

- PIPE SIZING AND SPRINKLERS ARRAY DESIGN

GENERAL REQUIREMENTS

SUPPLY MAINS: The nominal size of supply trunk mains and branch mains shall be not less than the size of any installation main distribution pipe, at its main installation control valve, supplied by the trunk main.

- INSTALLATION PIPEWORK: Individual sprinklers shall not be connected directly to distribution and main distribution pipes, except in the case of light-hazard installations where sprinkler may be connected directly to pipes not exceeding 50mm nominal bore.

- In ordinary or high-hazard installations arm pipes or drop pipes not exceeding 32 mm nominal bore shall be used to connect individual sprinklers where these are fed from pipes larger than 65mm nominal bore,

- Where upright or pendent conventional or spray sprinklers are fitted within 400 mm of the pipe axis alongside a pipe of nominal size greater than 65mm, the deflector shall be not more than the appropriate distance given in Table 14 above the lower edge of the pipe.

- ORIFICE PLATES:

- An orifice plate used to hydraulically balance an installation, or to accommodate pump characteristic, shall:

- have an orifice diameter not less than one-half of the internal diameter of the pipe into which it is fitted;

- be fitted only in pipes of 50 mm nominal bore or greater;

- be of brass or stainless steel with a plain central hole without burrs, and of a thickness complying with Table 15;

- have an identification tag, projecting beyond any flanges between which it is clamped, on which is clearly stamped the nominal pipe diameter and the orifice "K" factor. (also see rule 13.6)

- The orifice plate shall be fitted not less than two pipe internal diameters downstream of the outlet from any elbow or bend.

- The relationship between orifice size, flow rate and the pressure loss shall be calculated using the data given in Tables 31 and 32.

TABLE – 14

| Location of sprinklers alongside feed pipes larger than 65 mm nominal size |  |  |
| --- | --- | --- |
| Minimum horizontal distance from pipe centre line to the sprinkler centre line (mm) | Maximum height of sprinkler deflector above lower edge of pipe (mm) |  |
|  | Conventional sprinkler installed upright | Spray sprinkler upright/ pendent and conventional sprinkler pendent |
| 100 | 00 | 17 |
| 200 | 17 | 40 |
| 400 | 34 | 100 |

NOTE: Dimensions may be interpolated.

TABLE – 15

| Orifice Plate thickness according to pipe nominal bore Pipe nominal bore |  |  |
| --- | --- | --- |
| Pipe nominal bore (mm) |  | Orifice plate thickness (mm) |
| Over | Not greater than |  |
| -- | 80 | 3 |
| 80 | 150 | 6 |
| 150 | 200 | 9 |

- CONCEALED SPACES

- PROTECTION IN CONCEALED SPACES: Where there are concealed spaces above ceilings or below floors, and where the space below the ceiling or above the floor is classified as ordinary or high-hazard for which protection is specified in rule 11.8, the concealed spaces shall be protected as follows:

- if the concealed space contains only water pipes, electric wiring or air-conditioning trunking of non- combustible material by 10 mm sprinklers with a maximum area of coverage 21 M2 per sprinkler and a design density discharged of 5mm / min; or

- otherwise as specified for ordinary hazard.

The maximum area of sprinkler coverage and pipework design shall be as given in Table 16.

TABLE – 16

| SPRINKLER PROTECTION OF CONCEALED SPACES |  |  |  |  |
| --- | --- | --- | --- | --- |
| Class of protection in room |  | Concealed space pipework design |  | Concealed space maximum area per sprinkler, or treat as hazard class listed (in m2) |
| Pipework design method | Hazard class | Nominal size as for hazard class listed | AMAO as for hazard class listed |  |
|  | Light | Light | --- | Light |
| Pre- calculated | Ordinary | Ordinary | --- | 21 |
|  |  | Ordinary |  | Ordinary |
|  | High | Ordinary | --- | 21 |
|  |  | Ordinary |  | Ordinary |
|  | Light |  | Light | Light |
| Fully calculated | Ordinary |  | Ordinary | 21 |
|  |  |  | Ordinary | Ordinary |
|  | High |  | Ordinary | 21 |
|  |  |  | Ordinary | Ordinary |

- The feed pipe to the sprinklers in the concealed space shall be arranged and sized as follows:

- LIGHT HAZARD: The concealed space above or below shall be protected by a separate pipe from the installation valve.

- ORDINARY HAZARD: If the concealed space above a pre-calculated installation are fed individually from the pipework below, the range and distribution pipes in the installation shall be sized by taking the room and concealed space sprinklers cumulatively.  Alternatively if two feed pipes are used, one for the concealed space and one for the room sprinklers, the common feed pipe shall have a nominal bore of not less than 65 mm.

The concealed space below a pre-calculated installation shall be fed by two feed pipes, one for the concealed space and one for the room sprinklers, the common feed pipe shall have a nominal bore of not less than 65 mm.

- HIGH HAZARD: If the concealed space above or below a pre-calculated installation shall be fed by a separate feed pipe from that feeding the sprinklers in the room. The concealed sprinkler feed pipe shall be connected outside the room between the installation valve set and any 48-sprinkler design point for a high hazard sprinkler array outside the room concerned.

- FULLY HYDRAULICALLY CALCULATED INSTALLATION: The pressure and flow characteristics of the installation shall be satisfactory under each of the following operating conditions:

- When the appropriate density and AMAO are needed wholly in the room.

- When the appropriate density and the AMAO given in Table 16 are needed wholly in the concealed space.

- PRE-CALCULATED SPRINKLER ARRAYS:

GENERAL:

- The size of distribution feed pipes, including in light-hazard installations any which are partly range pipes because of the three sprinkler limitation, shall be as specified in the tables from the terminal point(s) up to the design point(s).

The feed pipe between the installation main control valves and the design point shall be hydraulically calculated on the basis of a maximum flow loss (specified in the appropriate sub-clause), corrected for static head gain for design points not at the highest level, at a particular flow rate.

Where the number of sprinklers in an array in a room, or in an area protected by a distinct group of sprinklers having its own distribution pipe spur, is less than or equal to the number of sprinklers for which the distribution pipes are hydraulically designed, the design point shall be positioned at the point of connection to the distribution pipe of the range of the array which is hydraulically nearest to the installation control valves.

Where the number of sprinklers in an array in a room on a distribution pipe terminal spur exceeds the number for which the distribution pipes are hydraulically designed, the design point shall be positioned at the point of connection to the range or ranges immediately upstream of the group of ranges containing not more than the maximum specified number of sprinklers beyond the design point.

Risers or drops, connecting ranges to distribution pipes and pipes longer than 300 mm connecting single sprinklers to distribution pipes, shall be considered to be distribution pipes and sized accordingly. The design point shall be positioned at the point of connection of the riser, drop or single sprinkler pipe to the horizontal distribution pipe run when designing the hydraulically determined length of feed pipe.

- Pipe diameters shall not increase in the direction of flow of water to any sprinkler.

LIGHT HAZARD:

RANGE AND TERMINAL SPUR DISTRIBUTION PIPES: The nominal size of range pipe and terminal distribution pipes, i.e. distribution pipes downstream of the design point, shall be as given in table 17.

NOTE: It is possible only under light hazard risks that sprinklers can be fed directly from the distribution pipes.

DISTRIBUTION PIPES (OTHER THAN TERMINAL SPURS): All pipework between the installation main control valves and the design point at each extremity of an installation array at the highest level shall be sized by hydraulic calculation using the values of the tables 18 and 19.

- DESIGN POINT: Normally it shall be two-sprinkler point.  However, under the following circumstances, it shall be three sprinkler point. (see figure 20)

- If the range pipe caters to 4 or more sprinklers; and

- When the range pipe runs along the apex of the ridge roof; or

- When the range pipe is the only line along a narrow room or corridor.

- Maximum number of sprinklers that can be fed from a range pipe shall not be more than six.

The pressure loss between the design point and the entry point from the distribution pipe to the range (where more than two sprinklers are provided in the range) shall be calculated as per the table 19 (column A).

The pressure loss from the entry point as said above at the extremity of the installation and the installation valve shall be calculated as per the table 19 (column B).

In case of sprinklers in different levels in the same risk, allowance can be given to the static pressure gain in the successive levels below the top most level. The nominal size of the distribution pipe shall however not be less than the minimum size specified in table 17 for the range pipe fed from the design point.

- The layout of the sprinkler installation shall, by and large, conform to the method shown in the Figure 20.

TABLE – 17

| Light hazard range and terminal distribution pipe sizes |  |  |  |
| --- | --- | --- | --- |
| Pipe | Size (mm) | Maximum length (in m) | Maximum number of |
|  | 20 | 8 | 1 |
| Steel | 25 | N.A | 3 |

*The limit of 3 sprinklers does not preclude the use of 25 mm pipe between the 2/3 sprinkler design point and the installation valve if hydraulic calculation shows it is possible nor does it follow that 25 mm pipe may be used between the 3rd and 4th sprinklers where the two sprinkler point is the design point.

TABLE - 18

MAXIMUM PIPE FLOW LOSS BETWEEN EACH DESIGN POINT AND THE

INSTALLATION CONTROL VALVE IN LIGHT HAZARD INSTALLATION

| DESIGN POINT | MAXIMUM FRICTION LOSS INCLUDING CHANGES OF DIRECTION (BARS) | DISTRIBUTION AND RANGE PIPE LOSS |
| --- | --- | --- |
| Two sprinkler point | 0.9 | See Column A and B of table 19 |
| Three sprinkler point | 0.7 | See Column B of table 19 |
| Two sprinkler point in a narrow room or range at roof apex each with a single line of three sprinklers | 0.7 | See Column B of table 19 |

TABLE – 19

| Pressure loss per unit length for design flow rates in light hazard installation |  |  |  |
| --- | --- | --- | --- |
| Pipe Material | Nominal size (mm) | Pressure loss per unit length (in m bar/m) |  |
|  |  | Column ‘A’ | Column ‘B’ |
| Steel (IS-1239) | 25 | 44.0 | 200.0 |
|  | 32 | 12.0 | 51.0 |
|  | 40 | 5.5 | 25.0 |
|  | 50 | 1.7 | 7.8 |
|  | 63 | 0.5 | 2.2 |

- The equivalent length of an elbow, bend or tee where the water is turned through an angle shall be taken as 2M in using the data or in using Table 29 or Table 30.

- Where heavy grade steel as per IS-1239 is used, flow rate shall be taken as 100 LPM for column B.

- ORDINARY HAZARD.

- RANGE PIPE AND TERMINAL DISTRIBUTION PIPE SIZES: The size of the nominal bores shall be as shown in the table 20 below.

TABLE - 20

RANGE PIPE NOMINAL SIZES FOR VARIOUS PIPE LAY OUTS IN

ORDINARY HAZARD INSTALLATIONS

| Range pipe layout | Pipe nominal bore (mm) | Maximum number of sprinklers to be fed by pipe of size listed |
| --- | --- | --- |
| Ranges at remote end of each distribution pipe spur - |  |  |
| - Last two ranges in two end-side layout | 25 32 | 1 2 |
| - Last three ranges in three end-side layout | 25 32 | 2 3 |
| - Last range in all other layouts | 25 32 40 50 | 2 3 4 9 |
| All other ranges | 25 32 40 50 | 3 4 6 9 |

A single sprinkler shall be fed by pipe of not less than 25 mm nominal bore.

There shall be not more than six sprinklers on any range, including apex range where the ranges run under a roof longitudinally, sloping at an angle that is greater than 6o .

- Distribution pipe (except terminal pipe): The main distribution and distribution pipes (including all risers and drops) between the highest design point and the installation valve shall be sized by hydraulic calculation based on table 21. The maximum friction loss shall not exceed 0.5 bars at a flow rate of 1000 LPM. The distribution pipes downstream the design point shall comply with sizes stated in table 22.  The layout of the installation shall, by and large, be in the same fashion as shown in Figure 21 (particularly for large installations) to enable hydraulic balance.

TABLE - 21

PRESSURE LOSS PER UNIT LENGTH FOR DESIGN FLOW RATES IN

ORDINARY HAZARD INSTALLATION

| Pipe nominal bore (IS-1239, Medium) (mm) | Pressure loss per unit length (m-bar/m) |
| --- | --- |
| 65 | 35 |
| 80 | 16 |
| 100 | 4.4 |
| 150 | 0.65 |
| 200 | 0.16 |

Note 1:  The equivalent length of an elbow, bend or tee where the water is turned through an angle shall be taken as 3 M when using the data or in using Table 29 or 30.

Note 2: Where heavy grade steel as per IS-1239 is used, flow rate shall be taken as 1000 LPM.

Pre- calculated distribution pipe nominal bores downstream of the design point shall comply with Table 22.

TABLE - 22

DISTRIBUTION PIPE NOMINAL SIZES IN ORDINARY HAZARD INSTALLATIONS AND MAXIMUM NUMBER OF SPRINKLERS DOWNSTREAM OF DESIGN POINT

| Pipe layout | Distribution pipe nominal size (mm) | Maximum number of sprinklers to be fed by pipe listed below |
| --- | --- | --- |
| - Two end -side | 32 40 50 65 | 2 4 8 16 |
| - All other types | 32 40 50 65 | 3 6 9 18* |

*This does not preclude the use of 65 mm nominal bore pipe between the 16/18 sprinkler point and the installation valves if hydraulically found in order.

- The feed pipe for all the other design points (except the highest design point) shall be similarly sized by hydraulic calculation. In case of friction loss in any part of the feed pipe not common with that feeding the highest design point, allowance can be given to the static pressure gain in the successive levels below the top most level. The nominal size of the distribution pipe shall however not be less than the minimum size specified in table 22 for the range pipe fed from the design point.

DESIGN POINT: The design point shall be 16-sprinkler point for two end-side sprinkler range pipe and the 18-sprinkler point for all other layouts. (Figure 21)

HIGH HAZARD

Range pipe and terminal distribution pipe sizes: Range pipes and nominal bores shall be as given in the table 23 or 24 depending on the sprinkler nominal size and the table in which the water supply-pressure flow characteristic is specified (i.e. tables 5, 6, 7 or 8).

TABLE - 23

RANGE PIPE NOMINAL SIZES FOR VARIOUS PIPE LAYOUTS FOR HIGH HAZARD INSTALLATIONS WITH SPRINKLERS OF 15MM NOMINAL

BORE AND PRESSURE FLOW CHARACTERISTICS

AS GIVEN IN TABLES 5 OR 6.

| Range pipe lay out | Pipe nominal size (mm) | Maximum number of sprinklers to be fed by pipe listed below |
| --- | --- | --- |
| Ranges at remote end of each distribution pipe spur - |  |  |
| Last two ranges in two end-side layout | 25 32 | 1 2 |
| Last three ranges in two end- side layout | 25 32 | 2 3 |
| Last range in all other directions | 25 32 40 | 2 3 4 |
| All other ranges | 25 32 | 3 4 |

TABLE - 24

RANGE PIPE NOMINAL SIZES FOR VARIOUS PIPES LAYOUTS FOR HIGH HAZARD INSTALLATIONS WITH SPRINKLERS OF 15 MM NOMINAL BORE AND PRESSURE FLOW CHARACTERISTICS AS GIVEN IN TABLE 7 OR OF 20 MM NOMINAL

SIZE AND PRESSURE FLOW CHARACTERISTICS AS GIVEN IN TABLE 8

| Range pipe layout | Pipe nominal size (mm) | Maximum number of sprinklers to be fed by pipe listed |
| --- | --- | --- |
| - End-side arrangements - - Last three ranges | 40 50 65 | 1 3 6 |
| - Other ranges | 32 40 50 65 | 1 2 4 6 |
| - End-center arrangements - Two end center layout - Last three ranges - Other ranges - Three and four end center layouts, all ranges | 32 40 32 32 40 50 | 1 2 2* 1 2 4 |

*32 mm feed to each

No range pipe shall be connected to a distribution pipe exceeding 150 mm nominal bore.

Pre-calculated distribution pipe nominal bores downstream of the design point shall be as given in table 25 or 26 depending upon the sprinkler head nominal size and the table in which the water supply pressure flow characteristic is specified (ie tables 5, 6, 7 or 8)

DISTRIBUTION PIPE UPSTREAM OF THE DESIGN POINT: The main distribution and distribution pipes between each sprinkler design point and the installation valve shall be sized by hydraulic calculation using the pipe friction loss per unit length given in the table 27 for the flow specified in rule 8.2.3.2.

TABLE - 25

DISTRIBUTION PIPE NOMINAL SIZES FOR VARIOUS NUMBERS OF SPRINKLERS DOWNSTREAM OF THE DESIGN POINT IN

HIGH HAZARD INSTALLATIONS WITH SPRINKLERS

OF 15 MM NOMINAL BORE AND PRESSURE

FLOW CHARACTERISTICS AS

GIVEN IN TABLE 5.

| Distribution pipe nominal size listed (mm) | Maximum number of sprinklers to be fed by the pipe of size |
| --- | --- |
| 32 | 2 |
| 40 | 4 |
| 50 | 8 |
| 65 | 12 |
| 80 | 18 |
| 100 | 48* |

*This does not preclude the use of 100 mm nominal size pipe between the design point and the installation valve if it is possible by hydraulic calculation requirements.( 12.4.4.4)

TABLE - 26

DISTRIBUTION PIPE NOMINAL SIZES FOR FEEDING VARIOUS NUMBERS OF SPRINKLERS DOWNSTREAM OF THE DESIGN POINT IN THE HIGH

HAZARD INSTALLATIONS WITH SPRINKLERS OF 15 MM NOMINAL

SIZE AND PRESSURE FLOW CHARACTERISTICS AS GIVEN IN

TABLE 6 OR 7 OR SPRINKLERS OF 20 MM NOMINAL SIZE

AND PRESSURE FLOW CHARACTERISTICS AS

GIVEN IN TABLE - 8.

| Range pipe layout | Distribution pipe nominal size (mm) | Maximum number of sprinklers to be fed by pipe listed |
| --- | --- | --- |
| Four end side layout | 65 | 8 |
| All other layouts | 50 65 80 100 150 | 4 8 12 16 48* |

*This does not preclude the use of 100 mm nominal size pipe    between the design point and the installation valve if it is possible by hydraulic calculation requirements.

TABLE - 27

PRESSURE LOSS PER UNIT LENGTH OF PIPE FOR DESIGN FLOW RATES

IN HIGH HAZARD INSTALLATIONS.

| Flow rate LPM | Pressure loss per unit length (m bar/m) |  |  |  |
| --- | --- | --- | --- | --- |
|  | 100 mm nominal size medium grade pipe (IS-1239) | 150 mm nominal size medium grade pipe (IS-1239) | 200 mm nominal size medium graded pipe (IS-1239) | 250 mm nominal size medium grade pipe (IS-1239) |
| 2800 4550 5600 6750 9000 | 34 72 115 160 250 | 5.1 11.0 16.0 23.0 36.0 | 1.3 2.7 4.1 5.8 9.1 | 0.43 0.90 1.40 1.85 3.00 |

Where other grades of pipes are used, pressure loss data shall accordingly change.

- The equivalent length of an elbow, bend or tee where the water is turned through an angle shall be taken as 3 M when using the data or in using Tables 29 or 30.

- DESIGN POINT: The design point shall be the 48-sprinkler point or if appropriate as specified in rules 8.2.3.2, 8.2.3.3 or 12.4.1.3 (Figures 22, 23, 24)

- The highest sprinkler shall be either downstream of a sprinkler design point or in an array with its own terminating distribution spur.

- The layout of the sprinkler installation shall, by and large, conform to the methods shown in the Fig. 22,23,24.

- The pressure loss in the distribution pipe to any particular section of the installation valve shall be adjusted to that needed to match the water supply characteristic by either:

suitably sizing the distribution pipe spur feeding the particular section when the distribution pipe nominal size shall not be less than that of the first length, sized by the pipe tables, of distribution pipe downstream of the design point to which it is connected, or  b) fitting an orifice plate complying with rule 12.2 in the particular distribution pipe.( see figures 22, 23, 24).

FULLY HYDRAULICALLY CALCULATED PIPE ARRAYS

GENERAL

The requirements of this clause apply to pipe arrays sized by full hydraulic calculation.

MINIMUM PIPE SIZES:  The nominal bore of main and other distribution pipes, and range pipes shall be not less than as follows:

| in a light-hazard installation | as given in table 54 for single sprinklers. |
| --- | --- |
| in an ordinary or high- hazard installation | 25mm |

MAXIMUM RANGE PIPE SIZE:  The nominal bore of range pipes shall be not more than 65mm, except where individual sprinklers are connected to pipes exceeding 65mm nominal bore when the arrangement shall comply with 12.1.

DENSITY OF DISCHARGE - The minimum density of discharge from each AMAO, or the entire protected area, whichever is the smaller, containing the relevant group of four sprinklers with each water supply or supply combination available shall be not less than the design density specified in Tables 2, 3 and 4.

Where possible the density of discharge shall be taken as the total flow from a group of four sprinklers which are most closely adjacent (in standard layout four sprinklers lying on the corners of a matrix cell square or rectangle, or in a staggered layout four sprinklers on the corners of a notional parallelogram), in L/min divided by four times the area (in M2) of the notional square, rectangle or parallelogram on the corners of which the sprinklers lie.  Where fewer than four sprinklers are in open communication, the minimum density shall be taken as the lowest value of the flow from any sprinkler divided by the area covered by the sprinkler.  The area covered shall be taken as that defined by the centre lines drawn midway between adjacent sprinklers at right angles to the line joining the sprinklers and by the boundary of the area covered (see figure 25).

MINIMUM SPRINKLER FLOW PRESSURE.  The calculated discharge pressure at roof or ceiling sprinkler, or an intermediate sprinkler, other than a rack or shelf sprinkler, when all the sprinklers in an AMAO plus the required number of any intermediate sprinklers are discharging simultaneously, and the predicted pressure at the 'C' gauge is available from the supply, shall be not less than as given in Table 28.

- NUMBER OF SPRINKLERS IN AMAO

The AMAO shall be either:

- as specified for each layout in section 8; or

- the area in open communication (i.e. where sprinklers may be expected to operate during the same fire incident) of the hazard class concerned;

(whichever is the smaller)

Where different hazard classes are in adjacent areas and in open communication the AMAO of the highest class shall apply and any excess area specified in clause 8.2.3.4 shall be assumed to be in operation in the hydraulically least favourable position in an adjacent part of the lesser hazard area.

Where the total area in open communication is less than the AMAO specified in section 8, the whole area shall be assumed to be in simultaneous operation.

NUMBER OF SPRINKLERS IN AMAO.  The number of sprinklers in simultaneous operation shall be integral and not less than N, given by the equation:

N    =  (A/a) + R      where

‘A’ is the roof or ceiling sprinkler AMAO (in m2);  ‘a’ is the mean floor area covered by each roof or ceiling sprinkler in the AMAO under consideration (in m2);  ‘R’ is the number of sprinklers located under obstructions in the area of operation.

- AREA COVERED BY INDIVIDUAL SPRINKLER.  In a square or rectangular matrix array the area covered by an individual sprinkler not on the boundary of the array shall be the floor area contained by the notional square or rectangle formed by the two centre lines between the sprinkler and the two adjacent sprinklers on the range, and the two centre lines between the range pipe carrying sprinkler and the two adjacent range pipes {see figure 26(a)}.

In a staggered array the area covered by an individual sprinkler shall be that of the floor area contained by a notional parallelogram formed by the centre lines between the range pipe carrying the sprinkler and the two adjacent range pipes and the lines joining points on the range pipe sections midway between the sprinkler and each of the two adjacent sprinklers on the range and the corresponding positions on the two adjacent ranges {see figure 26(b)}.

LOCATIONS OF AMAO

HYDRAULICALLY MOST UN-FAVOURABLE LOCATION:  Changes in sprinkler spacing, array design, elevation, range centres, sprinkler nominal orifice size and pipe sizes, as well as all possible locations, whether on the distribution pipes or between distribution pipes where these are connected by range pipes, shall be considered when determining the hydraulically most un-favourable location of the AMAO.

HYDRAULICALLY MOST FAVOURABLE LOCATION:

All possible locations, whether on the distribution pipes, or between distribution pipes where these are connected by ranges, shall be considered for the hydraulically most favourable location of the AMAO.

SHAPE OF AMAO

HYDRAULICALLY MOST UN-FAVOURABLE LOCATION.

The following shall be considered.

Terminal spur and looped distribution pipe installations with spur ranges in the hydraulically most un-favourable location the shape of the maximum AMAO shall be as near as possible rectangular.  One side shall be defined by the range, or range pair where there is an end-centre arrangement.

Sprinklers not constituting a full range or range pair shall be grouped as close as possible to the distribution pipe on the next upstream range row to the rectangular area {see figures 27(a), 27(b) and 27(c)}.

HYDRAULICALLY MOST FAVOURABLE LOCATION:

The following shall be considered.

TERMINAL SPUR AND LOOPED DISTRIBUTION PIPE INSTALLATIONS WITH SPUR RANGES:  In the hydraulically most favourable location the shape of the AMAO shall be as near as possible square, and shall where possible comprise sprinklers on one distribution pipe only.  The number of sprinklers calculated to be operating on ranges, or range pairs in end-centre installations, shall be located on each range or range pair at the hydraulically most favourable location.  Sprinklers not constituting a full range or range pair shall be located on the next range row at the hydraulically closest locations {see figures 27(b) and 27(c)}.

- INTERMEDIATE LEVEL IN-RACK SPRINKLERS

Where more than 50 intermediate level sprinklers are installed in the racks, roof and/or ceiling sprinklers in the concerned area along with the intermediate level sprinklers shall be installed with a separate installation control valve set.

For hydraulic calculation purpose, it shall be assumed that minimum of three sprinklers are operating simultaneously on each level up to a maximum of three levels at the hydraulically remote position. The minimum operating pressure in any sprinkler shall not be less than 2 bars.

In-rack sprinklers in association with the ceiling sprinklers shall always be fully calculated for the purpose of hydraulics.

+ + + + + + + + + +  +

- MISCELLANEOUS DESIGN PARAMETERS

- HYDRAULIC CALCULATION AND PIPE SIZING:

- Pipe size and layout shall be based on either :

- Full Hydraulic Calculation in which case the basic hydraulic performance shall be as specified in section 8 i.e. under "Design density and AMAO". Notwithstanding the density requirements as stated in this section, no roof or ceiling sprinklers in a fully hydraulically designed system shall discharge at a pressure less than the required as shown in table 28 as below:

TABLE – 28

MINIMUM SPRINKLER DISCHARGE PRESSURE AT ANY SPRINKLER IN FULLY HYDRAULICALLY CALCULATED INSTALLATIONS

| Hazard class | Minimum pressure at any discharging sprinkler (bar) |
| --- | --- |
| Light | 0.70 |
| Ordinary | 0.35 |
| High | 0.50 |
| In rack sprinklers | 2.00 |

- Pre-Calculated Installation (not including intermediate sprinklers), the pipe sizing tables with hydraulic calculation of portions of the feed pipe work as specified in rule 12.4.2 or 12.4.3 or 12.4.4 according to the class of hazard.

- Any extension to a pre-calculated installation shall not be fully hydraulically calculated.

- CALCULATION OF PIPEWORK LOSSES

- The static pressure difference between two interconnecting points in a system shall be calculated from:

Static pressure difference (ß)  = 0.1h (bar), where h = vertical distance between the points in meters

- PIPE FRICTION LOSS: Frictional pressure loss in pipes shall be calculated from the Hazen-Williams formula as under:

6.05 X 105

p =                                        X  L  X  Q1.85

C1.85 X d4.87

where	p = loss of pressure per meter length of pipe (bar)

Q = flow rate through the pipe (in LPM)

d = mean bore of the pipe (in M)

C = a constant for the type and condition of pipe

L = equivalent length of pipe and fittings (in M)

The following values shall be used for ‘C’ in sprinkler installations for calculation purpose:

cast iron                   =   100

mild steel                  =  120

galvanized steel        =  120

- Fittings and valve frictional losses: Frictional losses in valves and fittings where the direction of water flow is changed through 45° or more shall be calculated by the formula stated in rule 13.2.2 above using the appropriate equivalent length given in table 29 as below:

- The effect of velocity head can be ignored for the purpose of hydraulic calculation.

- The size of range pipe shall not be less than 25 mm and also the minimum pressure shall not be lower than those specified in rule 13.1.1 above.

- MAXIMUM FLOW DEMAND CALCULATION FOR A FULLY HYDRAULICALLY CALCULATED INSTALLATION

- The datum point for pressures and heights shall not be downstream from the control valve "C" gauge.

- At any pressure (P), the flow demand (Q) of the installation shall, be regarded as the sum of:

- the flow to the ceiling or roof sprinklers with the AMAO in the hydraulically most favourable location; plus

- the flow to any non-rack intermediate sprinklers associated with (a); plus

- c)   the simultaneous hydraulically balanced flow to any rack or shelf sprinklers in their specified number and hydraulically most favourable location.

TABLE - 29

EQUIVALENT LENGTH OF FITTINGS AND VALVES

| Fittings& valves | Equivalent length of medium grade steel pipe (in m) according to IS 1239 (C = 120) for diameter in mm equal to – |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 50 | 65 | 80 | 100 | 150 | 200 | 250 |
| Screwed elbow 90° | 1.46 | 1.89 | 2.37 | 3.04 | 4.30 | 5.67 | 7.42 |
| Welded elbow 90° | 0.69 | 0.88 | 1.10 | 1.43 | 2.00 | 2.64 | 3.35 |
| Screwed elbow 45° | 0.76 | 1.02 | 1.27 | 1.61 | 2.30 | 3.05 | 3.89 |
| All other fittings | 2.91 | 3.81 | 4.75 | 6.10 | 8.61 | 11.34 | 13.85 |
| Gate valve | 0.38 | 0.51 | 0.63 | 0.81 | 1.13 | 1.50 | 1.97 |
| Alarm valve/N.R valve |  |  | 3.94 | 5.07 | 7.17 | 9.40 | 12.30 |
| Alarm valve/N.R valve (Mush room) |  |  | 119.71 | 5.36 | 35.88 | 47.27 | 61.85 |
| Fittings& valves | Equivalent length of medium grade steel pipe (in M) according to IS 1239 (C = 120) for diameter in mm equal to: |  |  |  |  |  |  |
| Butterfly valve | 2.19 | 2.86 | 3.55 | 4.56 | 6.38 | 8.62 | 9.90 |
| Globe valve | 6.43 | 21.64 | 126.80 | 34.48 | 48.79 | 64.29 | 84.11 |

The equivalent lengths can be converted as necessary for pipes of cast iron by multiplying the above values by 0.714.

The equivalent length for sizes smaller than 50 mm are provided in the following table 30.

TABLE 30

EQUIVALENT LENGTH OF FITTINGS AND VALVES

| Fittings | Equivalent length (in m) of medium grade steel pipe (in m) according to IS 1239(C = 120) for diameter in mm equal to: |  |  |
| --- | --- | --- | --- |
|  | 25 | 32 | 40 |
| Screwed elbow 90° | 0.77 * | 1.04 | 1.22 |
| Welded elbow 90° | 0.36 * | 0.49 | 0.56 |
| Screwed elbow 45° | 0.40* | 0.55 | 0.66 |
| All other fittings | 1.54 | 2.13 | 2.44 |

*It is recommended to avoid, as far as possible, 25 mm sized elbows in the installation.

- The pressure-flow demand characteristics of the installation shall be determined either:

- by calculation (as stated in rule 13.3.2 above) of sufficient values of Q to determine the intercept of the installation characteristics of the curve with the water supply characteristic curve; or

- by calculation (as stated in rule 13.3.2 above) of a single value of Q from the equation:

P    = P0   + 0.1(h)  (Q/Q0)2   -- 0.1(h),   where

P      = pressure at flow Q measured at the datum point in bar.

Po  = pressure corresponding to the calculated installation flow demand measured at the datum point in bar.

Q     = flow demand at pressure P in LPM.

Qo   = Calculated installation flow demand in LPM for pressure Po.

h   = height of the highest sprinkler in the AMAO under conside-ration above the datum point in M.

By extrapolating the pressure flow demand graph to intersect the water supply pressure flow characteristic, Qmax can be determined.

- The maximum flow demand (Qmax) shall be regarded as the point of intersection of the pressure flow demand characteristic of the installation and the characteristic of the pump either at low water level or when the reservoir is full whichever is higher. (Figure no 28)

- At the maximum flow demand, the pressure at the datum point shall not be less than Po i.e. pressure corresponding to the calculated installation flow demand measured at the datum point in bar.

- MAXIMUM PRESSURE DEMAND CALCULATION FOR A FULLY HYDRAULICALLY CALCULATED INSTALLATION.

The calculation shall be as follows: - Pressure flow calculation shall be made for the minimum allowable density from the most remote group of four sprinklers in the AMAO hydraulically most remote from the installation valves (rules 8.1, 8.2, 8.3 and 12.5.4). Where there are both roof or ceiling sprinklers and intermediate sprinklers, the true hydraulically most un-favourable locations of each installation shall be taken together, irrespective of their actual locations in the building, the result can be extrapolated on to the water supply pressure flow characteristics curve of the pump as stated in rule 13.3.4 above.  The water supply pressure at the point of intersection of the curves shall not be less than that given by the minimum density calculation.

- HYDRAULIC BALANCE CALCULATIONS

- Balancing across junctions: Hydraulic calculations for each pipe junction where flows join or separate for each position of the AMAO or for each group of intermediate sprinklers assumed to be in operation shall be sufficiently accurate that:

- the calculated flow rate(s) into the junction are within ± 2LPM of the calculated flow rate(s) out of the junction;

- all values of the pressure calculated for the junction are within ± 0.005 bar of the mean value.

- Overall balancing of the installation: For each position of the AMAO the sum of the calculated sprinkler discharge values of all sprinklers discharging simultaneously (using the calculated nozzle pressure in each case to establish the outlet flow) shall be within ± 1% of the hydraulically calculated total flow into the installation.

- DESIGN OF ORIFICE PLATES

- The tables appearing in the next sheets can be used to design the size of the orifice plate according to the system requirement for achieving hydraulic balance.

- The tables provides the orifice diameter for medium grade pipes conforming to IS 1239 of sizes 50 mm to 200 mm for discrete values of net pressure loss Pro for a standard flow rate of 500 LPM in table no 33 and 5000 LPM in table 34.

- To select an orifice plate which will produce a net pressure loss of Prx bar with a rate of Qx in LPM, the value of Pro can be calculated from the formula as below:

Pro  = Px (500/Qx)2   when using table 31

Pro  = Px (5000/Qx)2 when using table 32

as appropriate, and refer to the appropriate column for the correct orifice diameter, interpolating as necessary.

The pressure loss produced by the orifice plate is the net loss across the orifice, not the pressure difference of the flange. The K factor shall be marked on the plate.

- COMPONENTS OF SPRINKLER SYSTEM

- GENERAL

- The various types of valves used in the installation are as under :

- Stop valves

- Test valves

- Drain valves

- Flushing valves.

- Check valves

- Installation valves

- Pre-action valves

- Subsidiary valves

- All valves in the sprinkler installation shall be right-handed (i.e. the hand wheel or key shall be rotated clockwise to close the valve); the direction of opening and closing shall be marked and an open/shut indicator fitted.

- Butterfly valves, if used, shall be of the gear- operated type for sizes more than 150 mm.

- Valves, which interlock when closed, shall be positioned in a conspicuous place where the key is obtrusive when the valve is closed.

- MAIN STOP VALVES

- One, and only one, main stop valve shall be fitted immediately downstream of the main alarm valve of a standard sprinkler installation.

- The main stop valve(s) shall be at a fire brigade access level and readily accessible when responding to a fire alarm.

- Where the working pressure of the installation is more than 7 Kg/cm², Cast iron valves with PN 1.6 rating shall be provided. However, Cast steel valves of class 150 shall suffice for installation under all pressure conditions.

- TEST VALVES AND COCKS

- Alarm and pump start test valves:  Test valves (15mm nominal size) shall be provided, as appropriate, to test:

- the hydraulic alarm or any electric alarm pressure switch if provided, by drawing water from the downstream side of a wet alarm valve, and any downstream main stop valve(s).

- Any water flow alarm switch installed downstream of the main installation valve set.  The test valve shall be connected downstream of the water flow alarm;

- An automatic starting device on a pump.

- Any pump house sprinkler alarm flow switch installed upstream of the installation control valve.

The test valve shall be installed close to the alarm valve, flow switch or pump starter as appropriate.

- TEST COCKS

A test cock shall be fitted as follows:

- on suction pump supplies, upstream of the pump outlet stop valve and the check valve;

- Immediately upstream of the check valve on a water supply feed pipe or trunk subject to any requirements of the inflow water authority.

- DRAIN VALVES

Drain valves sized as below shall be fitted to allow drainage from:

- Immediately downstream of the installation alarm valve or, if fitted, its downstream stop valve; and

- Immediately downstream of any subsidiary stop valve; and

- Any pipe other than drop pipes to single sprinklers in a wet installation, which cannot be drained through another drain valve.

The valves shall be fitted at the lower end of permanent pipework.  The outlet shall be not more than 3 m above the floor and shall be fitted with a brass plug.

| Light hazard | 40 mm |
| --- | --- |
| Ordinary hazard | 50 mm |
| High hazard | 50 mm |

- FLUSHING VALVES

Where a sprinkler pump draws water from a non-potable source such as a canal, river, lake etc., (with prior permission of the Committee) flushing valves shall be fitted at the spur ends of the installation distribution pipes.

The valves and any associated drain pipework shall be of the same nominal size as the distribution pipe to which they are attached.  Each valve outlet shall be fitted with a brass plug cap.

- CHECK VALVES

- Check valves shall be provided where more than one water supply is available and the same fitted on each water supply pipe to trunk main.

- A test cock shall be fitted upstream of the check valve and downstream of the water supply main stop valve, except in the case of a pump supply where it shall be upstream of the pump delivery check valve and of the outlet stop valve.

- SUBSIDIARY STOP VALVES

Subsidiary stop valves, which shall be of the same nominal size as the pipe in which they are fitted, shall be provided only to control the water supply to the following:

- Any sprinklers supplied from upstream of an installation main control valve set.

- Sprinklers under hoods over the dry ends of paper making machines where it is necessary to turn off the sprinklers to enable machine cylinders to be changed.  The valve shall be secured open.

- Sprinklers protecting a computer area.  The stop valve shall be electrically monitored or of the type, which interlocks when, closed, and in alternate installations shall be a screw-down diaphragm valve.

- INSTALLATION  AND ALARM VALVES

- A sprinkler installation shall be fitted with a suitable main installation valve to control the water supply to the installation. The valve set comprise of

- a main stop valve

- an alarm valve

- a water motor alarm and gong.  (Figure 29)

- The main installation alarm valve(s) shall be fitted immediately downstream of the main stop valve.

- An alarm valve controlling the water supply to either a high-temperature area or to an area where freezing temperatures may occur either shall be of a type without a water seal or positioned at such a distance from the protected area that the water seal is not affected by the high temperature or freezing.

- The main stop valve shall be placed in the vicinity of the main entrance of the risk protected at an easily accessible place. The valve shall be secured open by a pad- locked or rivetted strap and protected against impact damage.

- A plan of the risk with the position of main stop valves shall be placed in a conspicuous location. A location plate shall be fixed near the valves bearing the following words in raised letters:

S P R I N K L E R

S T O P   V A L V E

Figure 29 - Sprinkler Installation Valve assembly

- ALARM VALVE

- Alarm valves shall be fitted on the main supply pipe immediately above the main control valve and before any connection is taken off to supply any part of the installation.

- In buildings containing more than one installation, each alarm valve must have a number indicated thereon and the relevant alarm gong shall bear the same number in bold figures.

- As far as possible, one risk shall be protected by one alarm valve only. Where the risk is quite large and has to be fed by more than one valve, the areas fed by the alarm valves shall be planned and suitably demarcated. Details of the division of the sprinkler load with the demarcated areas shall be exhibited near the alarm valves.

- The provision of one alarm valve for different blocks in one compound is not normally permissible. The Committee shall be approached in advance with full particulars for acceptance under extraneous circumstances.

- MULTIPLE CONTROLS

Multiple controls installed to control open sprinklers or open drenchers or to operate a pressure switch shall be acceptable in specific cases upon reference to the Committee with full particulars in advance.

- ALARMS AND ALARM DEVICES

- Each installation main control valve set shall be provided with a water motor alarm suitable for sprinkler service located as close as possible to the alarm valve.

- The water motor shall be installed with its gong on the outside of an exterior wall and with its centre line not higher than 6 m above the point of connection to the alarm valve.  A strainer, readily accessible for cleaning, shall be fitted between the motor nozzle and the alarm valve connection.  The water outlet shall be positioned so that any flow of water can be seen.

- The pipework to the water motor shall be galvanized, medium grade complying with IS 1239.  The equivalent length of pipe between the alarm valve and the water motor shall be not more than 25 m assuming an equivalent length of 3 m for each change of direction.  The nominal size shall be not less than:

- 14 mm for equivalent lengths less than or equal to 6 m; and b) 20 mm for equivalent lengths greater than 6 m.

- The pipe shall be fitted with a stop valve located within the premises and shall be provided with a permanent drain through an orifice not larger than 3 mm diameter.  The orifice place may be integral with the pipefitting, and shall be of either stainless steel or a non-ferrous material.

- Any device to reduce the frequency of false or intermittent alarms fitted to the installation shall be suitable for sprinkler service.

- PRESSURE GAUGES

- GENERAL AND SPECIFICATION

- Pressure gauges fitted in the installations shall comply with relevant IS standards.

- The scale subdivision shall not exceed:

  - 0.2 bar for a maximum scale value up to and including 10 bar;

  - 0.5 bar for a maximum scale value of more than 10 bar, up to and including 16 bar;

  - 1.0 bar for a maximum scale value more than 16 bar.

- APPLICATION OF PRESSURE GAUGES.

- INSTALLATION CONTROL VALVES

MAIN CONTROL VALVE SETS:  A pressure gauge shall be fitted at each of the following points:

- Immediately downstream of the alarm valve (designated the `C` gauge); and

- Immediately upstream of the main control stop valve (designated the `B` gauge).

- WATER SUPPLY CONNECTIONS

PUMP SUPPLY:  Each pump supply shall be fitted with a damped pressure gauge on the supply pipe immediately downstream of the outlet check valve and upstream of any outlet stop valve.

- REMOVAL

Means shall be provided to enable each pressure gauge to be removed readily without interruption of the water or air supply to the installation.

- Any other provisions like fire brigade signaling from the alarm valves, Advance warning etc. proposed to be incorporated in the installation shall have prior approval of the Committee.

+ + +  + + + + +  +

- SPRINKLERS - GENERAL REQUIREMENTS

- GENERAL

- Sprinklers and Multiple controls installed in the Sprinkler systems shall be suitable for the fire protection service.

- Sprinklers shall not be reconditioned or repaired. Used and/or defective sprinklers shall be replaced by new ones.  However, the multiple control systems may be repaired or reconditioned but pressure testing shall be carried out before commissioning such installations.

- Sprinklers and multiple controls shall not be painted except for the identification purposes. They shall not be altered in any respect nor have any type of ornamentation or coating.

- SPRINKLER TYPES AND APPLICATIONS

- Sprinklers shall be of the following types:

- Conventional Pattern;

- Spray Pattern;

- Ceiling or flush pattern;

- Concealed pattern;

- Side wall pattern.

Note: - Pl. refer to the section ‘Definitions’ for the details on the above.

The selection of sprinklers shall conform to the Table 33 below.

TABLE – 33

SPRINKLER TYPES AND SIZES FOR VARIOUS HAZARD CLASSES

| Hazard class | Pattern of sprinkler | Sprinkler size nominal Orifice less than |
| --- | --- | --- |
| Light hazard | Spray, Ceiling or flush and/or side wall types | 10 mm |
| Ordinary hazard | Any type from the above | 15 mm |
| High hazard | Conventional or spray pattern only | 15 or 20mm as the case may be |

- CONVENTIONAL TYPE OF SPRINKLERS are designed to produce a spherical type of discharge with a proportion of water being thrown upwards the ceiling. These are usually built with a universal type deflector enabling the sprinklers to be installed either upright or pendent. It is also possible to designate them for upright or pendent for certain applications. These sprinklers can almost be used for any type of application. (Figure 30)

- SPRAY PATTERN TYPE SPRINKLERS are designed to produce a hemispherical discharge and no water is directed towards the ceiling. These are built both ways i.e. upright or pendent.  These shall not be used in high hazard, high piled storage risks and also in case of ordinary/high hazard class risks where there is exposed structural steel work or where the roof or ceiling or its supporting structure is of combustible material. (Figure 30)

- CEILING OR FLUSH AND CONCEALED TYPE OF SPRINKLERS are designed for use with the concealed pipework and are installed pendent with plate or base flush to the ceiling with the heat sensitive element below the ceiling line. These shall be installed only in light or ordinary hazard risks and not for the high hazard class. Common applications are Hotels, boardrooms, offices retail stores etc., where the aesthetic appearance is of value. The deflectors are normally fixed and if retracted type of deflectors are used, prior approval of the Committee is essential.

- SIDE WALL TYPE SPRINKLERS are designed to produce a downward paraboloidal discharge and the special deflector fitted to the sprinkler causes most of the water to be discharged on the opposing wall and floor with a little of water discharging on the wall behind the sprinkler. These shall not be installed in high hazard applications or above suspended ceilings. These are not substitutes for standard sprinklers but may be used only in offices, hotels, halls, lobbies, corridors, Conveyor housings etc.(see figure 30)

- MULTIPLE CONTROLS SYSTEM consists of heat sensitive sealed valve controlled outlets using sprinklers or any other heat detecting device as sensing elements.  Multiple control is used when a group of open sprinklers or sprayers have to operate simultaneously on a single detection according to the desired circumstances.

- SPRINKLER SIZE AND ‘K’ FACTOR:

Sprinklers shall have a nominal orifice sizes of 10 mm, 15 mm or 20 mm as shown in the Table 34.  ‘K’ factor of the sprinkler shall be as per the following equation.

K = Q /(P)0.5

Where K = K Factor, Q = Flow through the sprinkler orifice in                 LPM and P = pressure at the entry point of the sprinkler (bar)

The desired "K" factors for the sprinklers are shown in the Table 34.

TABLE – 34

SPRINKLERS NOMINAL THREADS, ORIFICE SIZES AND K FACTORS

| Nominal orifice size (mm) | Nominal thread size (mm) | Mean value of K factor | Limiting values of K factors |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Dry sprinklers |  | Others |  |
|  |  |  | Min | Max | Min | Max |
| 10 | 10 | 57 | 52 | 62 | 54 | 60 |
| 15 | 15 | 80 | 74 | 86 | 76 | 84 |
| 20 | 20 | 115 | 106 | 124 | 109 | 121 |

- TEMPERATURE RATING AND COLOUR CODING:

Sprinklers shall have one of the temperature ratings given in Tables 35 or table 36 and shall be correspondingly colour coded.

| TABLE - 35 | TABLE – 36 |
| --- | --- |

| Fusible link type |  |
| --- | --- |
| Temperature rating oC | Colour of yoke arms |
| 68/74 | Natural |
| 93/100 | White |
| 141 | Blue |
| 182 | Yellow |
| 227 | Red |

| # Glass Bulb type |  |
| --- | --- |
| Temperature rating o C | Colour of bulb liquid |
| 57 | Orange |
| 68 | Red |
| 79 | Yellow |
| 93 | Green |
| 141 | Blue |
| 182 | Mauve |
| 204/260 | Black |

- SELECTION OF TEMPERATURE RATING:

- GENERAL.

- The temperature rating of a sprinkler shall not be less than 30o C greater than the highest anticipated temperature of the location of the installation.

Note: - If the process conditions in a risk calls for continuous air conditioning round the clock throughout the year, relaxation may be considered upon reference to the Committee with full particulars.

- In high hazard installations protecting high piled storage with intermediate sprinklers, the roof or ceiling sprinklers shall have a temperature rating of 141o C.

Note:  - The sprinklers at the top of the racks shall be governed as per the previous rule 15.5.1.1

- Under glazed roof or where there are roof sheets of PVC or similar plastic material, the sprinkler rating shall be either 79o C to 100o C, or 141o C for high piled storage.

- The temperature rating of the roof or ceiling sprinklers within 3 M of the plan area of the boundary of either an oven or a hot process ventillating hood, fitted with sprinklers shall be the same as the oven or hood sprinklers, or 141o C, whichever is lower.

- PROTECTION TO THE SPRINKLERS: -

- Any sprinkler, other than ceiling or flush sprinkler. installed in a position at risk of accidental damage shall be fitted with a metal guard suitable for sprinkler service. It is particularly important for intermediate sprinklers in storage racks.

- Sprinklers installed in a rack or under a perforated shelf, platform and the like, where water from higher sprinklers including roof/ceiling sprinklers may cause wetting in close proximity to the bulb or fusible element shall be fitted with metal water shields of nominal diameter 80 mm. The shield shall not be directly attached to an upright sprinkler deflector or yoke assembly. Such shield shall form little or no obstructions the sprinkler spray pattern.

- Sprinkler rosettes shall be provided for the concealed sprinklers, which shall be of metal or thermoplastic plastics and shall be suitable for the sprinkler service.  No part of the rosette shall be used to support ceilings or other structures and shall project from the ceiling below the top of the visible portion of the heat sensitive element.

- Sprinklers and multiple controls installed in areas where corrosive vapours are prevalent shall have corrosion resistant coatings suitable to sprinkler service.  Frequent coating with good quality petroleum jelly is recommended. The coating shall however not be applied on the fusible links or the body of the glass bulb.

- SPARE SPRINKLERS TO BE KEPT IN STOCK:

- A stock of spare sprinklers shall be maintained in the premises so that prompt replacement is possible after the operation/damage of sprinkler heads. The spares shall be kept in an easily accessible location under conditions where the temperature does not exceed 38o C.

- The following guidelines shall be followed in respect of stocking spare sprinkler heads:

| Hazard Class | In all state capitals and within 100Km thereof | Other places |
| --- | --- | --- |
| Light Hazard | 6 sprinklers of each type | 25 |
| Ordinary Hazard | 24 sprinklers of each type | 50 |
| High Hazard | 36 sprinklers of each type | 100 |

When there is more than one installation within a risk, the above quantity shall also be increased in proportion. Each type of sprinkler used in the installation such as conventional or spray or ceiling/flush or sidewall sprinklers and appropriate temperatures shall be stocked as per the above requirements.

- Spanners for the sprinklers shall also be kept along with the spare sprinklers in readiness.

- DRAINAGE ARRANGEMENT

It shall be possible to drain the water from the entire installation through the installation control valve by opening the drain cock.  Normally, it is not permissible to provide separate arrangements for draining the water from different areas or pockets.  However, in case of sprinklers below the false ceilings, below the obstructions like ducts and also for intermediate sprinklers, it shall be possible to drain the water from time to time through separate arrangements.  In case of areas, where sprinklers are installed below the level of the installation control valve, it is necessary to provide drain cocks for all such sprinklers as deemed necessary.

+ + + + + + + + + +

- SELECTION OF INSTALLATION, TYPE AND THEIR SIZE

- A sprinkler installation shall be based on anyone of the following types:

- Wet pipe installation,

- Pre-action type installation,

- Recycling installation and

- Deluge installation.

Note: - Where circumstances warrant, Committee may allow other types of installations like alternate wet and dry pipe or dry pipe.  The Committee shall be approached in advance with full details for consideration.

- WET PIPE INSTALLATION

- A wet pipe system is a standard type sprinkler system permanently charged with water under pressure both above and below the installation alarm valve.  The above system shall be only installed where there is no danger at any time of the water in the pipes freezing.

- SIZE OF THE INSTALLATION: 	The number of sprinklers in an installation but not including the sprinklers in the concealed spaces and inside machines etc. shall not exceed the following:

| a) Light hazard | 500 per installation |
| --- | --- |
| b) Ordinary hazard | 1000 per installation |
| c) High hazard | 1000 per installation |

- PRE-ACTION INSTALLATION

A pre-action system is a sprinkler system installed only to prevent a premature discharge of water from pipework or sprinklers that have suffered mechanical damage.  The pipework shall normally be charged with air under pressure and monitored to give a warning indication on reduction of the air pressure.  Complete loss of air results in the opening of pre-action valve and thus allowing water into the pipework. The system at this stage becomes a wet pipe installation valve.  The system provides a pre-action time for the users to save their valuable equipment like EDP and computer installation, antiques, museums etc. where water damage due to the sprinkler operation is colossal. These systems need additional detection installations for triggering the pre-action valves.

- RECYCLING INSTALLATION

Recycling installations shall be used only where there are necessary for the following reasons:

- To restrict water damage after extinguishment;

- To avoid closure of the main installation valve if modifications are made to the pipework or if sprinkler heads are to be replaced;

- To prevent accidental water damage due to breakage of pipe work /sprinklers

These are similar to the pre action type installations except for the additional built in features for automatic control of the water by timers.

- SIZE OF THE INSTALLATION: The number of sprinklers in an installation (Pre action and recycling) but not including the sprinklers in the concealed spaces and inside machines etc., shall not exceed the following:

| a) Light hazard | 500 per installation |
| --- | --- |
| b) Ordinary hazard | 1000 per installation |
| c) High hazard | 1000 per installation |

- DELUGE INSTALLATIONS

Deluge installations shall be installed where it is necessary to apply water over an entire area in which a fire may originate. For detailed rules and regulations on the deluge systems, reference shall be made to the rules for water spray system published by the Committee

- MULTI-JET SPRINKLER SYSTEM

Under extraneous circumstances, the above type of systems can be considered for approval upon reference to the Committee with full particulars in advance. For example, the above system may be considered for installation within ducts, which pass through the perfect party walls if provision of dampers on both sides of the perfect party wall is impracticable. The above system shall consist of main sprinkler that shall operate a group of open sprinklers inside the duct on both sides of the wall. The main sprinkler shall be installed preferably in the centre of the wall within the duct. The open sprinklers are expected to provide water curtains within the ducts on both sides to prevent propagation of the fire through the ducts in the absence of dampers.

- DETECTOR SPRINKLERS

In locations where electrical installations are to be protected, sprinklers in such locations may act only as detectors and sound the installation alarm without discharge of water. The water from the sprinkler pipes may be suitably arranged to be by-passed outside the risk upon operation of sprinklers. The Committee shall be approached in advance with full particulars in such cases.

- OTHER TYPE OF SPRINKLERS

Where other types of sprinklers are used for special applications such as Fast response sprinklers, Early response quick suppression sprinklers, large orifice sprinklers, Recycling sprinklers etc., are proposed to be used in the system, Committee shall be approached in advance with full particulars for consideration.

++++++++

- UPKEEP OF THE SPRINKLER INSTALLATION

- GENERAL ARRANGEMENTS

The user shall carry out a programme of inspection and checks, arrange a test, service and maintenance schedule and keep appropriate records including a logbook, which shall be produced on demand.

- PRECAUTIONS AND PROCEDURES WHEN SYSTEM IS NOT OPERATIONAL.

- Maintenance, alterations and repair of systems not fully operational shall be carried out in a way that will minimize the time and extent of non-operability.

- When an installation is rendered inoperative, the user should implement compensatory measures. These measures include- shutting of fire doors and shutters, alertness of the security and safety staff, reinforcement of first aid appliances etc.,

- As much as possible of the installation shall be retained in an operative condition by blanking off pipework feeding the inoperative part or parts where work is taking place.

- In case of manufacturing risks, where the repairs and alterations are extensive, or it is necessary to disconnect a pipe exceeding 40mm nominal diameter, or to overhaul or to remove a main stop valve, alarm valve or check valve, every effort shall be made to carry out the work when the machinery is stopped.

- Any pump out of commission shall be isolated by means of the valves provided.

- PLANNED SHUT DOWN

- Authorities from the Insurance companies and Tariff advisory Committee shall be kept informed in addition to the other authorities before shutting of the installation for any reason whatsoever.

- A round through the risk shall be undertaken before a part or total shut down to ensure that there is no indication of fire.

- The heads of all the departments or blocks shall be notified in writing that the installation shall remain inoperative and they should exercise abundant caution during the period.

- UNPLANNED SHUT DOWN

When the installation is rendered inoperative as a matter of urgency or by accident, the measures stated above for planned shut down shall be implemented with least possible delay.

- ACTION FOLLOWING SPRINKLER OPERATION.

- Following the operation of sprinkler(s), the operated heads shall be removed and replaced with appropriate sprinkler heads and water supply shall be restored.

- The sprinklers in the vicinity of the operated sprinklers shall be checked for damage by heat or any other cause and replaced if necessary.

- The sprinkler pump shall not be shut off until the extinguishment of the fire. The starting of the pump shall be automatic and the stopping of the pump after an extinguishment shall be manual.

- PERIODICAL TESTING AND MAINTENANCE

- GENERAL

- Sprinkler systems require competent and effective care and maintenance to assure that they will perform their purpose effectively at the time of fire.  Systems shall be serviced and tested periodically by personnel trained in this work.  An inspection contract with a qualified agency for service, test, and operation at regular intervals is recommended.

- Operating and maintenance instructions and layout shall be available or can be posted at control room and/or at the fire station of the plant.  Selected plant personnel shall be trained and assigned the task of operating and maintaining the equipment.

- At weekly, or other frequent, regular scheduled plant inspection, equipment shall be checked visually for obvious defects such as broken or missing parts, external loading or other evidence of impaired protection.

- At least once a week the system shall be visually checked and the reading of various pressure gauges of each Installation valve shall be recorded.

- A trained pump man shall be available on all shifts and at all hours to operate the pump or whenever required.

- FIRE WATER RESERVOIRS/TANK

- It shall be ensured that firewater tank reservoirs are always full and free from any foreign materials.  The water level shall be recorded weekly.

- Depending upon quality of water, reservoirs shall be cleaned once in a year or two years and sludge formation shall be prevented.

- FIRE PUMPS

- All the fire pumps shall be run at least 5 minutes everyday.  During testing water level of priming tank, delivery pressures of pumps. speed. and also other parameters are to be checked and recorded.

- All pump glands shall be maintained in good working conditions and checked weekly.

- The bearing grease caps shall be checked once every week and refilled with fresh grease. if necessary.

- Starter contacts shall be cleaned every week.

- Insulation resistance of pump motors shall be examined once in every six months and record shall be maintained.

- Starting Mechanism of diesel engine must be checked, the battery charger and also the batteries must be maintained in effective conditions and the engine shall be run at least for 5 minutes every day.

- SPRINKLER SYSTEM INSTALLATION

- All piping shall be examined at intervals to determine its conditions. Frequency of inspections will be dependent upon local conditions and shall be examined once in a year.

- All the Installation valves and sprinkler installation and associated equipment shall be serviced and tested annually by qualified personnel.

- Discharge test of sprinklers shall be carried out at least once in six months.  After each operation, sprinklers shall be removed and cleaned, unless observations under flow conditions indicate this is not necessary.

- Manual checking devices shall be operated at least twice annually.

- When normally opened valves are closed following the system operation or test, suitable procedures shall be instituted to ensure that they are reopened and that the system is promptly restored to full normal operating condition.

- All sprinklers shall be inspected for proper positioning or test, external loading and corrosion and cleaned if necessary, based on experience but at least once in six months.

- The entire system shall be flushed at least once a year.

- It is important to ensure that the sprinkler bulbs are kept free from paint or dust (otherwise it may not function correctly) and that the bulbs are accessible and clearly identified for maintenance purposes.

- All the equipment pertaining to the sprinkler system shall be painted at least once in two years.

- INSTALLATION VALVE AND ALARM GONG ASSEMBLY

- The pressure gauge readings above and below the valves shall be monitored everyday at commencement of the first shift.

- The time taken for the operation of alarm gong after opening the drain valves shall be monitored every week and corrective actions taken in case of malfunction of alarm gong.

- The alarm gong assembly shall be checked thoroughly once in three months.

Ready-made maintenance chart and summary sheets for the hydraulic calculation are shown below:

PERIODICAL TESTING AND MAINTENANCE CHART

| SUBJECT | ACTIVITIES | DURATION |
| --- | --- | --- |
| - Reservoir | Level checking Cleaning | Weekly once In two years |
| - Pump | Running test Test flow Lubrication Gland Packing Overhaul | Daily 5 minutes Annually Quarterly Weekly Once in two years |
| - Engine | Running Lubrication Battery Load test Overhaul Fuel tank check | 5mins all days Quarterly Status weekly Annually Once in 2 years Daily |
| - Motor | Lubrication Starter contact checking Insulation resistance | Weekly Weekly Half yearly |
| - Main piping | Flushing Gauge pressure | Once in 2 years Check daily |
| - Sluice valves | Operation Gland packing Lubrication | Monthly Monthly Quarterly |
| - Installation valves | Operation Alarm check Overhaul Cleaning | Weekly Weekly Annually Quarterly |
| - Sprinklers | Cleaning Flow test | Quarterly Quarterly |
| - Detector element | Performance | Six monthly |
| - Sprinkler installation | Performance Physical check up of piping for seeing dislocation of support, wrong orientation over loading etc. | Quarterly Monthly |
| - Pressure gauges | Calibration | Annually |
| - Painting of installation |  | Every two years |

HYDRAULIC CALCULATIONS - GENERAL: -

SUMMARY SHEET

The Summary Sheet should contain the following informations:-

- Date

- Location

- Name of Owner and Occupant

- Building or Plant Unit Number

- Description of Hazard

- Name and Address of Contractor

- Design Purpose (Type of System)

- Minimum Rate of Water Application

- Total water requirement as calculated including Hydrant System where applicable

- Water Supply information in detail.

- Risk wise details showing the total discharge and pressure at the top 	of Installation valve.

DETAILED WORKING SHEET

Detailed working sheet or Computer Print-out Sheets should contain the following informations

- Identification of calculation covered.

- Description and discharge constant (K) for the type of sprinkler used.

- Hydraulic design reference points

- Flow in LPM

- Pipe size (mm)

- Pipe lengths in meter and details of fittings.

- Equivalent pipe lengths for fittings and devices in Mts.

- Friction loss in bars/meter.

- Total friction loss between reference points in bars.

- Elevation head in bars between reference points.

- Required pressure in bars at each reference point

- Design details of Orifice plates

- Velocity pressure and normal pressure if included in calculations.

- Notes to indicate starting points with reference to other sheets or to clarify data shown

- Where extending existing system hydraulic calculations are to be furnished indicating the previous design, flow and pressure at points of connection and adequate additional calculations to indicate the effect on existing system.

+ + + + + + + + +

- PRE-COMMISSIONING AND ACCEPTANCE TESTS

- INSTALLATION PIPEWORK.

- All installation pipework shall be pressure tested in accordance with rule 10.1.6 which reads as under:

"The installation piping (from the pump house up to the installation valve and also the installation piping with sprinklers) shall be capable of withstanding for two hours a pressure equivalent to 150% of the maximum working pressure."

Note: - In water sensitive areas, it is advisable to test the pipes pneumatically before carrying out any hydraulic testing.

- The coating and wrapping of the underground wrought or mild steel pipes shall be carried out and also subjected to "Haliday" tests as per IS-10221.

- INITIAL TESTING TO REGULAR TESTING PROCEDURES.

The system shall be tested as specified in rules 17.6.2, 17.6.3 and 17.6.4 i.e. making the initial tests which shall become routine tests later as a part of upkeep of the system.

- WATER SUPPLIES

- The entire piping system shall be thoroughly flushed before commissioning in order to remove foreign materials which might have entered or be present in the system piping during the course of installation or which may have been present in existing piping at maximum flow rate available to the system consideration shall be given to the disposal of water discharged during the flushing.

- In case of large installations [where the number of sprinklers in a single building and those in the buildings communicating therewith exceed 500], it is necessary to ascertain the hydraulic balance to check the performance of the pump when working at most favourable and un-favourable locations. Pressure at the outlets of the orifice plates shall be measured at all locations to check the correctness of the size of orifice plates selected.

- Each installation valve shall be tested separately. The pump shall start automatically and the supply pressure at the appropriate flow rate shall not be less than the appropriate value specified in rules 8.2 and 8.3 for all types of hazards.

- The drain valves fitted above the installation valve shall be opened and the time taken for the alarm gong to operate be noted. There shall not be a significant variation in the timing between the 15mm and 50mm drain valves fitted above the installation valve to drain the water from the installation.

- PUMP OUTPUT

A running pressure test shall be carried out at the delivery of the pump at full load conditions (Qmax). The pressure obtained in the test can be used to correct the pressure available at the "C" gauge of the installation valve.

- AUTO START OF DIESEL PUMPS

When commissioning the installation the automatic starting system of the diesel engine driven pump set shall be activated with the fuel supply isolated for six cycles each of not less than 15 seconds cranking and at not more than 15 seconds rest. After completion of six starting cycles "the fail to start alarm" shall operate. The fuel supply shall then be restored and the pump set shall start when the manual start button is operated.

- INSTALLATION VALVES

- All the valves shall be physically checked for proper installation and leakage if any. The reading of the pressure gauges shall be checked to see whether they match after a few drain tests.

- The proper functions of the alarm gong associated with the installation valve and its level of audibility shall be checked. An audibility level of 85 db above the background noise level is required.

+ + + + + +  + +

- FEA DISCOUNT APPLICATION FORM FOR SPRINKLER INSTALLATION

APPENDIX I

Date:

The Asst. General Manager,

TARIFF ADVISORY COMMITTEE

__________REGIONAL OFFICE.

Dear Sir,

APPLICATION FOR FIRE EXTINGUISHING APPLIANCE(S) DISCOUNT

Risk (Name of the Factory)___________________________

Location ______________________________

As the above Insured have installed sprinkler system in the following blocks, kindly sanction as from the date of receipt of this application a discount of _________%.

(The Occupation floorwise and Block No. must be stated)

1. ____________________________________________________

2. ____________________________________________________

3. ____________________________________________________

I/We enclose plan of the risk with all details marked thereon.

I/We certify that to the best of my/our knowledge and belief the appliances referred to have been installed in strict accordance with the Rules of the Committee and I/We also certify that the plan submitted is drawn in accordance with the Committee`s Rules and is correct and up-to-date.

I/We also certify that a copy of the plan exact in every detail, is available at the above premises for the use of Committee`s Engineer.

I/We enclose full particulars of the appliances together with letter of Guarantee signed by the Assured.

Yours faithfully

(Branch Mgr./Divl.Mgr.)

For use of the TAC`s Regional Office only

Date received:                                                       Date inspected:

Discount sanctioned:                                          Reference Number:

APPENDIX II

Date:  ____________

The Asst. General Manager,

TARIFF ADVISORY COMMITTEE,

___________REGIONAL OFFICE.

Dear Sir,

GUARANTEE REGARDING FIRE EXTINGUISHING APPLIANCE(S)

In consideration of your Regional Office granting a Discount for the Fire Extinguishing Appliances detailed on attached/signed form which we have installed in the (name of factory)____________________________________

situated at _________________________________________________

We hereby engage ourselves: -

- To maintain and upkeep the said appliances in efficient working order and where such appliances and Committee’s Rules require the upkeep of a trained Fire Fighting Personnel to maintain such personnel in an efficient state.

- To advise the concerned Regional Office and first obtain permission should at any time it be necessary to close down supply to pumps or in any way render the appliances out of operation for repairs, overhaul etc.

- Not to extend, alter or demolish protected Blocks/Equipment or to erect new Block/Equipment in the compound of the premises without supplying the concerned Regional Office with a revised plan or revising the plan filed with the concerned Regional Office.

- To keep at the above described premises a copy exact in every detail of the plan supplied to your Regional Office, same to be available to the Regional Office`s Engineer during his visits of inspection.

- Not to re-number (or re-letter) Blocks, Compartments, etc. as recorded on the plan filed with the Regional Office without advising the Regional Office of such revision.

Yours faithfully,

(AUTHORISED SIGNATORY OF THE INSURED )

Note: All communication to the Regional Office of the Committee must be through the Leading Office on the risk.

APPENDIX III

Details of Automatic Sprinkler Protection System available at(Name of factory)________________________________________

| - DETAILS OF THE INSTALLATION: |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| - Pump(s) |  | No.1 | No.2 | No.3 | No.4 | Jockey |
| Type(s) - centrifugal or vertical turbine etc. Name plate details Makers name Type/model Impeller size Discharge Head Serial number R.P.M |  |  |  |  |  |  |
| - Prime mover(s) Type(s)- electrical motor/engine driven Name plate details Makers name Type/model Horse power/BHP/KW Serial number Voltage/current R.P.M Type of insulation Fuel tank capacity (L) |  |  |  |  |  |  |
| - Make and type of automatic regulator |  |  |  |  |  |  |
| - Water supplies |  |  |  |  |  |  |
| - Source of water supplies/ inflow arrangement for fire water reservoir |  |  |  |  |  |  |
| - Water reservoir |  |  |  |  |  |  |
| System | Demand m3 |  | Resv.1 | Resv.2 | Resv. 3 | Remarks |
|  |  |  | Actual provision Fire protection requirements |  |  |  |
| Sprinkler Spray Hydrant Foam |  |  |  |  |  |  |

Note 1: Specify whether the reservoirs are underground, surface or       overhead.

Note 2:   Give details on whether the tanks have independent/common suction  or whether the tanks are interconnected

- DETAILS OF SPRINKLER INSTALLATION

| Sl. No | Installation control valves |  |  |  |  | Blocks protected | Sprinklers |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Size & type | Make | Pressure available & |  | Orifice plate details |  | Type | Make | Nos |
|  |  |  | Above | Below |  |  |  |  |  |

- PIPES

| Underground/above ground |  |
| --- | --- |
| Type and method of joining |  |
| Make |  |
| IS or other equivalent specification |  |
| Details of Coating/ wrapping, if any |  |
| To what pressure have the pipes been tested |  |

- TESTING AND MAINTENANCE OF THE SYSTEM:

  - Whether the Installation Control valves/alarm bell provided at the premises tested/examined/operated at least once in 3 months.

  - Frequency of checking/cleaning of valve seat.

  - Frequency of pump(s) testing with remarks.

  - Are the records of all tests and defects maintained.

  - Number of Sprinkler Heads : readily available at stock.

Place:

Date:

SIGNATURE.

(FORM TO BE SIGNED BY THE OWNER OF THE PREMISES).

+ + + + +  + + + +